## Project Summary
|  |  |  | S-Quad & S-Cubed Visual Alarm Estimate Summary | [6 empty] | 2015-03-20
Project name
20th March 2015
Room ID | Room Name | Preferred Detector /Sounder Spacing | VAD Spacing | Ambient Light | VAD Colour | Line of Sight | Part Ref | Part Desc | Quantity | Length | Width | Ceiling Height | Mounting Height | Device setting | Certified Category | Corrected coverage | *** Max Mounting Height | *** Max Spacing of VAD
Note on C10: Simon: Preferred Spacing

## Background
EN54 - 23:2010 | Project Name | 20th March 2015
| Room | Room 1
| VAD colour | White
| Room Dims | 10m x 5m
Visual Alarm Estimator's Tool | Ceiling Height | 2.5m
| Ambient Light Level | Well Below Average (100 to 200 Lux)

## Sheet1 (hidden)
Room ID | Room Name | Detector Spacing | VAD Spacing | Ambient Light | Device Colour | Line of Sight | Room Length | Width | Mounting Height | Area of Room | Red / High Output | Red / Med Output | Red / Low Output | White / High Output | White / Med Output | White / Low Output | White / Low Output | Device Type | Quantity | Certified Category | *** Max Mounting Height | *** Max Spacing of VAD

## Table 1 (hidden)
Colour |  |  |  | Direct/Indirect |  |  |  |  | Ambient Light |  |  |  |  | Type |  | Ceiling VAD ratings | [5 empty] | Wall VAD Ratings
[9 empty] | Measured Ambient | Look up | [7 empty] | Certifed Cats | Heigth | Diam |  |  |  | Certifed Cats | Height | Cuboid |  | Filter for part number selection
1 | Red |  |  | 1 | Direct |  |  |  | 550 |  |  |  |  | 1 | Ceiling | Red / High Output | 1 | C-4.5-14 | 4.5 | 14 |  | Red / High Output | High Power | W-6.7-14 | 6.7 | 14
2 | White |  |  | 2 | Indirect | [8 empty] | 2 | Wall | Red / Med Output | 2 | C-4-13 | 4 | 13 |  | Red / Med Output | Medium Power | W-6.5-12.5 | 6.5 | 12.5 |  |  | 0 | #N/A | 1 | VAD only
|  |  |  | 3 | Direct | [8 empty] | 1 | High Power | Red / Low Output | 3 | C-3-10 | 3 | 10 |  | Red / Low Output | Low Power | W-5-9.5 | 5 | 9.5 |  |  | 0 | #N/A | 2 | Voice and VAD
|  |  |  | 4 | Indirect |  |  |  |  | Correction Factor |  |  |  | 2 | Standard | White / High Output | 4 | C-6-16 | 6 | 16 |  | White / High Output | High Power | W-5-12.5 | 5 | 12.5 |  |  | 0 | #N/A | 3 | Sounder and VAD
[15 empty] | W- | White / Med Output | 5 | C-5-14 | 5 | 14 |  | White / Med Output | Medium Power | W-4.5-11.3 | 4.5 | 11.3 |  |  | 0 | #N/A | 1 | Indoor
[10 empty] | 3 |  |  |  |  | Wall | White / Low Output | 6 | C-4-10.8 | 4 | 10.8 |  | White / Low Output | Low Power | W-3-8.5 | 3 | 8.5 |  |  |  |  | 2 | Outdoor
[14 empty] | 2 | Wall | White / Standard | 7 | C-3-10 | 3 | 10 |  | White / Standard | N/A - Power not configurable | W-3-8.5 | 3 | 8.5
Selected VAD Colour = White |  |  |  | Viewing Angle = Direct |  |  |  |  | Correction Factor | 1.4 |  |  |  | 1 | High Power | White / High Output *** |  | C-6-16 |  |  |  | White / High Output *** | High Power | W-5-12.5 | 5 | 12.5
[16 empty] | Red / High Output *** |  | C-4.5-14 |  |  |  | Red / High Output *** | High Power | W-6.7-14 | 6.7 | 14
[16 empty] | Red / Standard | 8 | C-3-10 | 3 | 10 |  | Red / Standard | N/A - Power not configurable | W-3-8.5 | 3 | 8.5
[10 empty] | 1 | Ceiling mount direct view | Ceiling mount indirect view | Wall mount direct view | Wall mount indirect view |  |  | 11.8861 | 5.9431 | 35.32 |  |  |  |  | 46.7925
Ceiling height |  |  |  | Sensor Spacing |  |  | Lux level |  |  | (lux) | [5 empty] | White / High Output *** | 7 | Diam |  | White / Low Output |  |  |  |  | 12.96 | 31.36 | 44.32 | 6.6573
[7 empty] | 99 |  |  |  | 2.8 | 1.3 | 5.2 | 1.8 |  | White / High Output | 7 | 17.5 | 17.5 |  | 1.4 |  | 21.8461
41 |  |  |  | 21 | 10 |  | 199 |  |  |  | 2.4 | 1.2 | 4.4 | 1.7 |  | White / Med Output | 6.3 | 15.82 | 15.82 | Wall | Direct |  | 19.5967
[7 empty] | 299 |  |  |  | 1.9 | 1 | 3.2 | 1.4 |  | White / Low Output | 4.2 | 11.9 | 11.9 | White | 150 |  | 13.681
0 | 0 |  | Dets for length | 1 |  | Spacing | 399 |  |  |  | 1.4 | 0.8 | 2.3 | 1.2 |  | White / Standard | 4.2 | 11.9 | 11.9 | 2.5 | 10 |  | 13.681
|  |  | Dets for width | 1 |  | 10.5 | 499 |  |  |  | 1.1 | 0.6 | 1.8 | 1 |  |  |  | Spacing |  | 2.5 | 0
|  |  | Total Dets | 1 |  |  | 599 |  |  |  | 0.9 | 0.5 | 1.3 | 0.9 |  | White / High Output |  | 17.5 | 12.4 |  | 5 | 10
|  |  | Det Spacing | 10 |  |  | 699 |  |  |  | 0.7 | 0.4 | 1 | 0.7 |  | White / Med Output |  | 15.8 | 11.2 |  |  | 5 | a
|  |  |  | 5 |  | Heat - Corridor | 800 |  |  |  | 0.5 | 0.3 | 0.7 | 0.6 |  | White / Low Output |  | 11.9 | 8.5 |  |  |  | i
|  |  | Ideal | 10 | [11 empty] | White / Standard |  | 11.9 | 8.5
|  |  | Adjusted | 10 |  | 10 | [9 empty] | White / High Output *** |  | 17.5 | 12.4
[16 empty] | Red / High Output *** |  | 17.5 | 12.4
[5 empty] | hhhhhh | [13 empty] | White / Low Output
[15 empty] | power setting | Low Power |  |  | White / Low Output |  | White / Low Output
[15 empty] | 17.5 |  |  | W-4.2-11.9 | 4.2 | 11.9 | 4.2 | 11.9
[15 empty] | loop load | LOOP Load |  | max spacing | 11.9 |  | 8.5
1 | [14 empty] | certified category | W-3-8.5 |  | Spacing OK
[16 empty] | Wall |  | Max Height | 4.2 |  | FALSE
Red / High Output | 0 | [13 empty] | S3-S-VAD-HPR-R / S3 Sndr/High Perf Red VAD/Red Body |  |  | Height OK
Red / Med Output | 0 | [13 empty] | S3 Sndr/High Perf Red VAD/Red Body | S3-S-VAD-HPR-R
Red / Low Output | 0 | [15 empty] | Colour | Type |  | Indoor | Check for filter | Sounder | Standard or High power
White / High Output | 0 | [13 empty] | O2H Sensor - Red VAD | S4-711-VAD-HPR | 1 | 1 | O2H Sensor - Red VAD | 1 | TRUE | 1 | 1
White / Med Output | 0 | [13 empty] | O2H Voice Sensor Sounder - Red VAD | S4-711-V-VAD-HPR | 1 | 1 | O2H Voice Sensor Sounder - Red VAD | 1 | TRUE | 2 | 1
White / Low Output | 1 | [13 empty] | O2HCO Voice Sensor Sounder - Red VAD | S4-911-V-VAD-HPR | 1 | 1 | O2HCO Voice Sensor Sounder - Red VAD | 1 | TRUE | 2 | 1
White / Standard | 0 | [13 empty] | HEAT Voice Sensor Sounder - Red VAD | S4-720-V-VAD-HPR | 1 | 1 | HEAT Voice Sensor Sounder - Red VAD | 1 | TRUE | 2 | 1
[15 empty] | O2H Sensor - White VAD | S4-711-VAD-HPW | 2 | 1 | O2H Sensor - White VAD | 1 | TRUE | 1 | 1
[15 empty] | O2H Voice Sensor Sounder - White VAD | S4-711-V-VAD-HPW | 2 | 1 | O2H Voice Sensor Sounder - White VAD | 1 | TRUE | 2 | 1
[15 empty] | O2HCO Voice Sensor Sndr - White VAD | S4-911-V-VAD-HPW | 2 | 1 | O2HCO Voice Sensor Sndr - White VAD | 1 | TRUE | 2 | 1
Check Room Name | 3 | [13 empty] | Heat Voice Sensor Sounder - White VAD | S4-720-V-VAD-HPW | 2 | 1 | Heat Voice Sensor Sounder - White VAD | 1 | TRUE | 2 | 1
[15 empty] | O2H Voice Sensor Sounder - Red VAD (standared power) | S4-711-V-VAD-LPR | 1 | 1 | O2H Voice Sensor Sounder - Red VAD (standard) | 1 | TRUE | 1 | 2
[15 empty] | O2H Voice Sensor Sounder - White VAD (standared power) | S4-711-V-VAD-LPW | 2 | 1 | O2H Voice Sensor Sounder - White VAD (standard) | 1 | TRUE | 2 | 2
[15 empty] | S3 Sounder/Red Body | S3-S-R | 0 | 3 | S3 Sounder/Red Body | 1 | TRUE
[15 empty] | S3 Voice Sounder/Red Body | S3-V-R | 0 | 3 | S3 Voice Sounder/Red Body | 1 | TRUE
[15 empty] | S3 Sounder/White Body | S3-S-W | 0 | 3 | S3 Sounder/White Body | 1 | TRUE
[15 empty] | S3 Voice Sounder/White Body | S3-V-W | 0 | 3 | S3 Voice Sounder/White Body | 1 | TRUE
[15 empty] | S3 VAD/HP White VAD/Red body | S3-VAD-HPW-R | 2 | 2 | S3 VAD/HP White VAD/Red body | 1 | TRUE | 1 | 1
[15 empty] | S3 High Perfromance Red VAD/Red Body | S3-VAD-HPR-R | 1 | 2 | S3 High Perfromance Red VAD/Red Body | 1 | TRUE | 1 | 1
[15 empty] | S3 Sounder/HP White VAD/Red Body | S3-S-VAD-HPW-R | 2 | 2 | S3 Sounder/HP White VAD/Red Body | 1 | TRUE | 3 | 1
[15 empty] | S3 Sndr/High Perf Red VAD/Red Body | S3-S-VAD-HPR-R | 1 | 2 | S3 Sndr/High Perf Red VAD/Red Body | 1 | TRUE | 3 | 1
[15 empty] | S3 Sounder/HP White VAD/White Body | S3-S-VAD-HPW-W | 2 | 2 | S3 Sounder/HP White VAD/White Body | 1 | TRUE | 3 | 1
[15 empty] | S3 Sndr/High Perf Red VAD/White Body | S3-S-VAD-HPR-W | 1 | 2 | S3 Sndr/High Perf Red VAD/White Body | 1 | TRUE | 3 | 1
[15 empty] | S3 Voice Sndr/HP White VAD/Red Body | S3-V-VAD-HPW-R | 2 | 2 | S3 Voice Sndr/HP White VAD/Red Body | 1 | TRUE | 2 | 1
[15 empty] | S3 Voice Sndr/HP Red VAD/Red Body | S3-V-VAD-HPR-R | 1 | 2 | S3 Voice Sndr/HP Red VAD/Red Body | 1 | TRUE | 2 | 1
[15 empty] | S3 Sounder/Red Body/IP66 | S3EP-S-R | 0 | 2 | S3 Sounder/Red Body/IP66 | 1 | TRUE
[15 empty] | S3 VAD/HP White VAD/Red Body/IP66 | S3EP-VAD-HPW-R | 2 | 2 | S3 VAD/HP White VAD/Red Body/IP66 | 2 | TRUE | 1 | 1
[15 empty] | S3 VAD/HP Red VAD/Red Body/IP66 | S3EP-VAD-HPR-R | 1 | 2 | S3 VAD/HP Red VAD/Red Body/IP66 | 2 | TRUE | 1 | 1
[15 empty] | S3 Voice Sndr/HP White VAD/Red Body/IP66 | S3EP-V-VAD-HPW-R | 2 | 2 | S3 Voice Sndr/HP White VAD/Red Body/IP66 | 2 | TRUE | 2 | 1
[15 empty] | S3 Voice Sndr/HP Red VAD/Red Body/IP66 | S3EP-V-VAD-HPR-R | 1 | 2 | S3 Voice Sndr/HP Red VAD/Red Body/IP66 | 2 | TRUE | 2 | 1
[15 empty] | SenTri/Sounder/Red Body | SEN-S-R | 0 | 2 | SenTri/Sounder/Red Body | 1 | TRUE
[15 empty] | SenTri/White High Performance VAD | SEN-VAD-HPW-R | 2 | 2 | SenTri/White High Performance VAD | 1 | TRUE | 1 | 1
[15 empty] | SenTri/Red High Performance VAD | SEN-VAD-HPR-R | 1 | 2 | SenTri/Red High Performance VAD | 1 | TRUE | 1 | 1
[15 empty] | SenTri Sounder/HP White VAD/Red Body | SEN-S-VAD-HPW-R | 2 | 2 | SenTri Sounder/HP White VAD/Red Body | 1 | TRUE | 3 | 1
[15 empty] | SenTri Voice Sndr/Red VAD/White Body | SEN-S-VAD-HPR-R | 1 | 2 | SenTri Voice Sndr/Red VAD/White Body | 1 | TRUE | 3 | 1
[15 empty] | SenTri/Sounder/Red Body/IP66 | SEN-S-EP-R | 0 | 2 | SenTri/Sounder/Red Body/IP66 | 2 | TRUE | 3 | 1
[15 empty] | SenTri/Sounder/White HP VAD/IP66 | SEN-S-VAD-HPW-EP-R | 2 | 2 | SenTri/Sounder/White HP VAD/IP66 | 2 | TRUE | 3 | 1
[15 empty] | SenTri/Sounder/Red HP VAD/IP66 | SEN-S-VAD-HPR-EP-R | 1 | 2 | SenTri/Sounder/Red HP VAD/IP66 | 2 | TRUE | 3 | 1
[15 empty] | S3 Sounder/Standard power White VAD/Red Body | S3-S-VAD-LPW-R | 2 | 2 | S3 Sounder/Standard power White VAD/Red Body | 1 | TRUE | 3 | 2
[15 empty] | S3 Sndr/Standard Power Red VAD/Red Body | S3-S-VAD-LPR-R | 1 | 2 | S3 Sndr/Standard Power Red VAD/Red Body | 1 | TRUE | 3 | 2
[16 empty] | SEN-770-VAD-HPW | 2 | 1 |  | 1 | TRUE | 3 | 1
[16 empty] | SEN-780-VAD-HPW | 2 | 1 |  | 1 | TRUE | 3 | 1
[16 empty] | SEN-770-VAD-HPR | 1 | 1 |  | 1 | TRUE | 3 | 1
[16 empty] | SEN-780-VAD-HPR | 1 | 1 |  | 1 | TRUE | 3 | 1
redstandard ceiling
[14 empty] | 1 | O2H Sensor - Red VAD | S4-711-VAD-HPR |  | S4-711-VAD-HPR (O2H Sensor - Red VAD)
[14 empty] | 2 | O2H Voice Sensor Sounder - Red VAD | S4-711-V-VAD-HPR |  | S4-711-V-VAD-HPR (O2H Voice Sensor Sounder - Red VAD)
[14 empty] | 3 | O2HCO Voice Sensor Sounder - Red VAD | S4-911-V-VAD-HPR |  | S4-911-V-VAD-HPR (O2HCO Voice Sensor Sounder - Red VAD)
[14 empty] | 4 | HEAT Voice Sensor Sounder - Red VAD | S4-720-V-VAD-HPR |  | S4-720-V-VAD-HPR (HEAT Voice Sensor Sounder - Red VAD)
[14 empty] | 5 | O2H Voice Sensor Sounder - Red VAD (LPR) | S4-711-V-VAD-LPR |  | S4-711-V-VAD-LPR (O2H Voice Sensor Sounder - Red VAD (LPR))
redHP ceiling
[15 empty] | O2H Sensor - Red VAD | S4-711-VAD-HPR |  | S4-711-VAD-HPR (O2H Sensor - Red VAD)
[15 empty] | O2H Voice Sensor Sounder - Red VAD | S4-711-V-VAD-HPR |  | S4-711-V-VAD-HPR (O2H Voice Sensor Sounder - Red VAD)
[15 empty] | O2HCO Voice Sensor Sounder - Red VAD | S4-911-V-VAD-HPR |  | S4-911-V-VAD-HPR (O2HCO Voice Sensor Sounder - Red VAD)
[15 empty] | HEAT Voice Sensor Sounder - Red VAD | S4-720-V-VAD-HPR |  | S4-720-V-VAD-HPR (HEAT Voice Sensor Sounder - Red VAD)
[15 empty] | O2H Sensor - White VAD | S4-711-VAD-HPW |  | S4-711-VAD-HPW (O2H Sensor - White VAD )
[15 empty] | O2H Voice Sensor Sounder - White VAD | S4-711-V-VAD-HPW |  | S4-711-V-VAD-HPW (O2H Voice Sensor Sounder - White VAD )
[15 empty] | O2HCO Voice Sensor Sndr - White VAD | S4-911-V-VAD-HPW |  | S4-911-V-VAD-HPW (O2HCO Voice Sensor Sndr - White VAD )
[15 empty] | Heat Voice Sensor Sounder - White VAD | S4-720-V-VAD-HPW |  | S4-720-V-VAD-HPW (Heat Voice Sensor Sounder - White VAD )
[15 empty] | O2H Voice Sensor Sounder - White VAD (LPW) | S4-711-V-VAD-LPW |  | S4-711-V-VAD-LPW (O2H Voice Sensor Sounder - White VAD (LPW))
[15 empty] | O2H Sensor - White VAD | S4-711-VAD-HPW |  | S4-711-VAD-HPW (O2H Sensor - White VAD )
[15 empty] | O2H Voice Sensor Sounder - White VAD | S4-711-V-VAD-HPW |  | S4-711-V-VAD-HPW (O2H Voice Sensor Sounder - White VAD )
[15 empty] | O2HCO Voice Sensor Sndr - White VAD | S4-911-V-VAD-HPW |  | S4-911-V-VAD-HPW (O2HCO Voice Sensor Sndr - White VAD )
[15 empty] | Heat Voice Sensor Sounder - White VAD | S4-720-V-VAD-HPW |  | S4-720-V-VAD-HPW (Heat Voice Sensor Sounder - White VAD )
[15 empty] | S3 High Perfromance Red VAD/Red Body | S3-VAD-HPR-R |  | S3-VAD-HPR-R (S3 High Perfromance Red VAD/Red Body)
[15 empty] | S3 Sndr/High Perf Red VAD/Red Body | S3-S-VAD-HPR-R |  | S3-S-VAD-HPR-R (S3 Sndr/High Perf Red VAD/Red Body)
[15 empty] | S3 Sndr/High Perf Red VAD/White Body | S3-S-VAD-HPR-W |  | S3-S-VAD-HPR-W (S3 Sndr/High Perf Red VAD/White Body)
[15 empty] | S3 Voice Sndr/HP Red VAD/Red Body | S3-V-VAD-HPR-R |  | S3-V-VAD-HPR-R (S3 Voice Sndr/HP Red VAD/Red Body)
[15 empty] | S3 VAD/HP Red VAD/Red Body/IP66 | S3EP-VAD-HPR-R |  | S3EP-VAD-HPR-R (S3 VAD/HP Red VAD/Red Body/IP66)
[15 empty] | S3 Voice Sndr/HP Red VAD/Red Body/IP66 | S3EP-V-VAD-HPR-R |  | S3EP-V-VAD-HPR-R (S3 Voice Sndr/HP Red VAD/Red Body/IP66)
[15 empty] | S3 Sndr/Standard Power Red VAD/Red Body | S3-S-VAD-LPR-R |  | S3-S-VAD-LPR-R (S3 Sndr/Standard Power Red VAD/Red Body)
[15 empty] | S3 High Perfromance Red VAD/Red Body | S3-VAD-HPR-R |  | S3-VAD-HPR-R (S3 High Perfromance Red VAD/Red Body)
[15 empty] | S3 Sndr/High Perf Red VAD/Red Body | S3-S-VAD-HPR-R |  | S3-S-VAD-HPR-R (S3 Sndr/High Perf Red VAD/Red Body)
[15 empty] | S3 Sndr/High Perf Red VAD/White Body | S3-S-VAD-HPR-W |  | S3-S-VAD-HPR-W (S3 Sndr/High Perf Red VAD/White Body)
[15 empty] | S3 Voice Sndr/HP Red VAD/Red Body | S3-V-VAD-HPR-R |  | S3-V-VAD-HPR-R (S3 Voice Sndr/HP Red VAD/Red Body)
[15 empty] | S3 VAD/HP Red VAD/Red Body/IP66 | S3EP-VAD-HPR-R |  | S3EP-VAD-HPR-R (S3 VAD/HP Red VAD/Red Body/IP66)
[15 empty] | S3 Voice Sndr/HP Red VAD/Red Body/IP66 | S3EP-V-VAD-HPR-R |  | S3EP-V-VAD-HPR-R (S3 Voice Sndr/HP Red VAD/Red Body/IP66)
[15 empty] | S3 VAD/HP White VAD/Red body | S3-VAD-HPW-R |  | S3-VAD-HPW-R (S3 VAD/HP White VAD/Red body)
[15 empty] | S3 Sounder/HP White VAD/Red Body | S3-S-VAD-HPW-R |  | S3-S-VAD-HPW-R (S3 Sounder/HP White VAD/Red Body)
[15 empty] | S3 Sounder/HP White VAD/White Body | S3-S-VAD-HPW-W |  | S3-S-VAD-HPW-W (S3 Sounder/HP White VAD/White Body)
[15 empty] | S3 Voice Sndr/HP White VAD/Red Body | S3-V-VAD-HPW-R |  | S3-V-VAD-HPW-R (S3 Voice Sndr/HP White VAD/Red Body)
[15 empty] | S3 VAD/HP White VAD/Red Body/IP66 | S3EP-VAD-HPW-R |  | S3EP-VAD-HPW-R (S3 VAD/HP White VAD/Red Body/IP66)
[15 empty] | S3 Voice Sndr/HP White VAD/Red Body/IP66 | S3EP-V-VAD-HPW-R |  | S3EP-V-VAD-HPW-R (S3 Voice Sndr/HP White VAD/Red Body/IP66)
[15 empty] | S3 Sounder/Standard power White VAD/Red Body | S3-S-VAD-LPW-R |  | S3-S-VAD-LPW-R (S3 Sounder/Standard power White VAD/Red Body)
[15 empty] | S3 VAD/HP White VAD/Red body | S3-VAD-HPW-R |  | S3-VAD-HPW-R (S3 VAD/HP White VAD/Red body)
[15 empty] | S3 Sounder/HP White VAD/Red Body | S3-S-VAD-HPW-R |  | S3-S-VAD-HPW-R (S3 Sounder/HP White VAD/Red Body)
[15 empty] | S3 Sounder/HP White VAD/White Body | S3-S-VAD-HPW-W |  | S3-S-VAD-HPW-W (S3 Sounder/HP White VAD/White Body)
[15 empty] | S3 Voice Sndr/HP White VAD/Red Body | S3-V-VAD-HPW-R |  | S3-V-VAD-HPW-R (S3 Voice Sndr/HP White VAD/Red Body)
[15 empty] | S3 VAD/HP White VAD/Red Body/IP66 | S3EP-VAD-HPW-R |  | S3EP-VAD-HPW-R (S3 VAD/HP White VAD/Red Body/IP66)
[15 empty] | S3 Voice Sndr/HP White VAD/Red Body/IP66 | S3EP-V-VAD-HPW-R |  | S3EP-V-VAD-HPW-R (S3 Voice Sndr/HP White VAD/Red Body/IP66)
[15 empty] | S3 VAD/HP Red VAD/Red body | S3-VAD-HPR-R |  | S3-VAD-HPR-R (S3 VAD/HP Red VAD/Red body)
[15 empty] | S3 VAD/HP Red VAD/Red Body/IP66 | S3EP-VAD-HPR-R |  | S3EP-VAD-HPR-R (S3 VAD/HP Red VAD/Red Body/IP66)
[15 empty] | S3 VAD/HP White VAD/Red body | S3-VAD-HPW-R |  | S3-VAD-HPW-R (S3 VAD/HP White VAD/Red body)
[15 empty] | S3 VAD/HP White VAD/Red Body/IP66 | S3EP-VAD-HPW-R |  | S3EP-VAD-HPW-R (S3 VAD/HP White VAD/Red Body/IP66)
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
[12 empty] | 0 | 0 | 0 | 0 | 0
Not Set
Note on AD4: Simon: filter type (ceiling or wall)
Note on AD5: Simon: Filter colour
Note on U28: Simon: Max diameter
Note on T29: Simon: Max spacing
Note on T31: Simon: Max Height

## Sheet2 (hidden)
Project Name | Colour |  | Ceiling Height | Line of sight |  | Ambient Light |  |  | 20th March 2015 |  | Light Level | Ceiling direct | Ceiling indirect | Wall direct | Wall indirect | Length of Room | Width of room | Height of Room | Wall Mount Height | Target SPL | Sounder Spacing |  |  |  |  | 93
20th March 2015 | 2 | White | 2.5 | 1 | Direct | 150 | 2 |  |  | 1 | Dark < 100 Lux | 2.8 | 1.3 | 5.2 | 1.8 | 10 | 5 | 2.5 | 5 | 65 | 20 |  |  | FALSE | 1 | 90
1 |  |  | Wall Height | line of sight wall |  | Well Below Average (100 to 200 Lux) |  |  |  | 2 | Well Below Average (100 to 200 Lux) | 2.4 | 1.2 | 4.4 | 1.7 |  | 1 |  |  | set required SPL |  | 0 |  | FALSE | 1.5 | 87
Room Name Check |  |  | 2.4 | 1 | Direct |  |  |  |  | 3 | Below Average (200 to 300 Lux) | 1.9 | 1 | 3.2 | 1.4 |  | 1 |  |  | 65 |  |  |  | FALSE | 2 | 84
3 | [9 empty] | 4 | Just Below Average (300 to 400 Lux) | 1.4 | 0.8 | 2.3 | 1.2 |  | 1 | [5 empty] | TRUE | FALSE | 3 | 81
Room 1 | 0 | Room 1 |  |  |  | VAD options for - - - Room 1 - - - - - 20th March 2015 |  | 20 | March | 5 | Just Above Average (400 to 500 Lux) | 1.1 | 0.6 | 1.8 | 1 |  | 1 | [6 empty] | FALSE | 4 | 78
Room Dimension | Length | Width |  |  |  |  | Room Number |  | 2015 | 6 | Above Average (500 to 600 Lux) | 0.9 | 0.5 | 1.3 | 0.9 |  | 1 | [6 empty] | FALSE | 6 | 75
| 10 | 5 |  |  |  |  | 1 |  |  | 7 | Well Above Average (600 to 700 Lux) | 0.7 | 0.4 | 1 | 0.7 |  | 1 | [5 empty] | 0 | FALSE | 8 | 72
[10 empty] | 8 | Bright Light (700 to 800 Lux) | 0.5 | 0.3 | 0.7 | 0.6 |  | 1 | [5 empty] | -3 | FALSE | 12 | 69
Detection Tech | Open or Corridoor |  |  |  |  | 10.5 |  |  |  |  | *** Above 600 Lux it is recommended a lighting specialist is consulted for advice | [5 empty] | 1 | [5 empty] | -6 | FALSE | 16 | 66
Smoke | Open Area | [15 empty] | 1 | [5 empty] | -12 | TRUE | 24 | 63
1 |  | Ceiling Active |  |  | TRUE |  | Wall active |  | Wal Sdr Y/N | [7 empty] | 1 | [5 empty] | -15 | FALSE | 32 | 60
Smoke - Open Area | Smoke - Open Area - nominal spacing 10.5m | 1 |  |  |  |  | 1 |  | 1 | [7 empty] | 1 | [5 empty] | -18 | FALSE | 48 | 57
Ceiling | [5 empty] | Wall | [6 empty] | Heat - Corridor | 10.5 |  |  | 1 | [5 empty] | -24 | FALSE | 64 | 54
Colour | 2 | White |  |  |  | Colour | 2 | White |  |  |  |  | Heat - Open Area | 7.5 |  |  | 1 | [5 empty] | -27 | FALSE |  | 51
Ceiling Height | 2.5 |  |  |  |  | Mounting Height | 2.4 | [5 empty] | Smoke - Corridor | 15 |  |  | 1 | [6 empty] | FALSE |  | 48
| 1 | Direct |  |  |  | Line of sight | 1 | Direct |  |  |  |  | Smoke - Open Area | 10.5 |  |  | 1
Ambient | 2 | 150 | Well Below Average (100 to 200 Lux) |  |  |  | 2 | 150 | Well Below Average (100 to 200 Lux) | [7 empty] | 1
correction factor | 2.4 |  |  |  |  | correction factor | 4.4 | [9 empty] | 1
[8 empty] | Calculated Max Sdr Spacing | ambient sound level | Required SPL |  |  | 1 | January |  |  | 1
Smoke det spacing | 10.5 |  |  |  |  | Sounder spacing | 20 | 48 | 60 | 65 |  |  | 2 | February |  |  | 1
[7 empty] | Max spacing for sounders - 20m | [5 empty] | 3 | March |  |  | 1
No of points for Detection | Width | Length |  |  |  | No of sounders | Width | Length |  |  |  |  | 4 | April
| 1 | 1 |  |  |  |  | 1 | 1 |  |  |  |  | 5 | May
Total Dets (just for smoke detection | 1 |  |  |  |  | Total Sdrs (just for sound) | 1 | [5 empty] | 6 | June |  |  | 1
Spacing (width) | Spacing (Length) | Ideal Spacing |  |  |  | Spacing (width) | Spacing (Length) | Ideal Spacing |  |  |  |  | 7 | July
5 | 10 | 10 | Detector quantity - 1 @ spacing of 10m |  |  | 5 | 10 | 10 |  |  |  |  | 8 | August
| Detector spacing = 10m | [11 empty] | 9 | September
Ceiling VAD ratings | [5 empty] | Wall VAD Ratings | [6 empty] | 10 | October |  |  | 1
|  | Certifed Cats | Height | Diam |  |  |  | Certifed Cats | Height | Cuboid |  |  | 11 | November |  |  | 1
Red / High Output | 1 | C-4.5-14 | 4.5 | 14 |  | Red / High Output | High Power | W-6.7-14 | 6.7 | 14 |  |  | 12 | December
Red / Med Output | 2 | C-4-13 | 4 | 13 |  | Red / Med Output | Medium Power | W-6.5-12.5 | 6.5 | 12.5
Red / Low Output | 3 | C-3-10 | 3 | 10 |  | Red / Low Output | Low Power | W-5-9.5 | 5 | 9.5
White / High Output | 4 | C-6-16 | 6 | 16 |  | White / High Output | High Power | W-5-12.5 | 5 | 12.5
White / Med Output | 5 | C-5-14 | 5 | 14 |  | White / Med Output | Medium Power | W-4.5-11.3 | 4.5 | 11.3
White / Low Output | 6 | C-4-10.8 | 4 | 10.8 |  | White / Low Output | Low Power | W-3-8.5 | 3 | 8.5
White / Standard | 7 | C-3-10 | 3 | 10 |  | White / Standard | N/A - Power not configurable | W-3-8.5 | 3 | 8.5
White / High Output *** |  | C-6-16 |  |  |  | White / High Output *** | High Power | W-5-12.5 | 5 | 12.5
Red / High Output *** |  | C-4.5-14 |  |  |  | Red / High Output *** | High Power | W-6.7-14 | 6.7 | 14
Red / Standard | 8 | C-3-10 | 3 | 10 |  | Red / Standard | N/A - Power not configurable | W-3-8.5 | 3 | 8.5
| Height | Diam | Spacing |  |  |  | Max Height | Spacing
White / High Output | 14.4 | 38.4 | 27.2 | 4 |  | White / High Output | 22 | 55 | 4
White / Med Output | 12 | 33.6 | 23.8 | 3 |  | White / Med Output | 19.8 | 49.72 | 3
White / Low Output | 9.6 | 25.92 | 18.3 | 2 |  | White / Low Output | 13.2 | 37.4 | 2
White / Standard | 7.2 | 24 | 17 | 1 |  | White / Standard | 13.2 | 37.4 | 1
White / High Output *** | 14.4 | 38.4 | 27.2 | 5 |  | White / High Output *** | 22 | 55 | 5
Detector spacing
| Height | Spacing |  |  |  |  | Height | Spacing
Best fit | White / Standard | White / Standard |  |  |  | Best fit | White / Standard | White / Standard
Recommended | White / Standard | White / Low Output |  |  |  | Recommended | White / Standard | White / Low Output
Coverage Best fit | 7.2 | 17 |  |  |  | Coverage Best fit | 13.2 | 37.4
Coverage recommended | 9.6 | 18.3 |  |  |  | Coverage recommended | 13.2 | 37.4
| 1 | 2 |  |  |  |  | 1 | 2
| White / Low Output | [5 empty] | White / Low Output
| Heigth OK | Spacing OK |  |  |  |  | Heigth OK | Spacing OK
Size of Room
Best fit | White / Standard | White / Standard |  |  |  | Best fit | White / Standard | White / Standard
Recommended | White / Standard | White / Low Output |  |  |  | Recommended | White / Standard | White / Standard
Coverage Best fit | 7.2 | 17 |  |  |  | Coverage Best fit | 13.2 | 37.4
Coverage recommended | 9.6 | 18.3 |  |  |  | Coverage recommended | 13.2 | 37.4
| 1 | 2 |  |  |  |  | 1 | 1
| White / Low Output | [5 empty] | White / Standard
| Heigth OK | Spacing OK |  |  |  |  | Heigth OK | Spacing OK
Calculate Qty |  | Margin allowed Factor |  |  |  |  | IF(spacingreccwall<=((C72)*spacingidealsdr),spacingreccwall,spacingidealsdr)
VAD Spacing | 10 | 100% |  |  |  | Spacing | 10
Quantity | width | Length |  |  |  | Quantity | width | Length
| 1 | 1 |  |  |  |  | 1 | 1
Qty of points | 1 |  |  |  |  | Qty of wall devices | 1
Design Coverage | 5 | 10 | 10 |  |  | Design Coverage | 5 | 10 | 10
Design Spacing
Best fit | White / Standard | White / Standard |  |  |  | Best fit | White / Standard | White / Standard
Recommended | White / Standard | White / Standard |  |  |  |  | White / Standard | White / Standard
Rated Coverage Best fit | 7.2 | 17 | [5 empty] | 37.4 |  |  | OR(selectedwallvad="White / Standard",selectedwallvad="Red / Standard",selectedceilingvad="Red / Standard",selectedceilingvad="White / Standard")
Coverage recommended | 9.6 | 17 | [5 empty] | 37.4 |  |  | TRUE | TRUE
| 1 | 1 |  |  |  |  | 1 | 1 |  |  | FALSE
| White / Standard | [5 empty] | White / Standard |  |  |  | White / Low Power
| Heigth OK | Spacing OK |  |  |  |  | Heigth OK | Spacing OK |  |  | White / Low Power
White / Standard
|  | White / Low Output | Height OK |  |  |  |  | White / Low Output
Selected VAD | White / Standard | STANDARD | Difference in height |  |  |  | White / Standard | STANDARD |  |  | White / Standard |  | S3-S-VAD-LPW-R
Max Height | 7.2 | 9.6 | 0 |  |  |  | 13.2 | 13.2 |  |  | Red / Standard |  | S3-S-VAD-LPR-R
Max Spacing | 17 | 18.3 |  |  |  |  | 37.4 | 37.4 |  |  |  |  | S4-711-V-VAD-LPR
Quantity | 1 |  |  |  |  | Quantity | 1 | [5 empty] | S4-711-V-VAD-LPW
Certified Rating | C-3-10 | C-4-10.8 |  |  |  |  | W-3-8.5 | W-3-8.5 |  |  | 0
Corrected Rating | C-7.2-24.1 | C - 9.6 - 25.9 |  |  |  |  | W - 13.2 - 37.4 | W - 13.2 - 37.4 |  |  |  | FALSE
Selected Colour | White | [5 empty] | White |  |  |  | FALSE
selected view | Direct | [5 empty] | Direct
Ceiling Height | 2.5 |  |  |  |  | Wall Mount Height | 2.4
Actual Spacing | 10
IF(Wall_Sdr_Y_N=0,"none",
|  | Direct |  |  |  | White
|  |  | Well Below Average (100 to 200 Lux) |  |  |  |  | S4-711-VAD-HPW (O2H Sensor - White VAD )
S3-VAD-HPW-R (S3 VAD/HP White VAD/Red body)
| Intensity | Qty
VADcolour
part Numbers | 1
2
3
4
5
6
7
|  |  | 20 x 15 x 3 |  |  |  | Large Room
|  |  | Direct |  | Indirect |  |  | Ceiling |  | Wall
Int | Q |  | Wall | Ceiling | Wall | Ceiling |  | Intensity | Qty | Intensity | Qty
0 | 2 | 50 | 1 | 4 | 1 | 4 | 50 | 3 | 4 | 3 | 1
0 | 2 | 150 | 1 | 4 | 1 | 4 | 150 | 3 | 4 | 3 | 1
3 | 2 | 250 | 1 | 4 | 2 | 6 | 250 | 3 | 6 | 3 | 2
3 | 4 | 350 | 1 | 4 | 2 | 6 | 350 | 4 | 6 | 3 | 2
4 | 6 | 450 | 1 | 4 | 4 | 12 | 450 | 4 | 12 | 3 | 4
4 | 6 | 550 | 2 | 6 | 4 | 20 | 550 | 4 | 20 | 3 | 4
4 | 6 | 650 | 4 | 9 | 6 | 20 | 650 | 4 | 20 | 3 | 6
4 | 6 | 750 | 6 | 20 | 6 | 35 | 750 | 4 | 35 | 3 | 6
|  |  | Intensity (W) | Qty (W)
1 | 4 | 1
1 | 4 | 1
1 | 4 | 1 | Intensity | 1 | 50 |  | 2
3 | 4 | 1 | 0 | 1 | 150 | 1 | 2
3 | 4 | 1 | 0 | 1 | 250 | 1 | 2
3 | 6 | 2 | 0 | 1 | 350 | 1 | 2
4 | 9 | 2 | 0 | 1 | 450 | 3 | 2
4 | 20 | 2 | 2 | 1 | 550 | 3 | 2
|  |  | 3 | 1 | 650 | 4 | 4
|  |  | 3 | 2 | 750 | 4 | 6
Note on B72: Simon: Suggest 10% factor before reducing spacing
Note on A76: Simon: This is the coverage of VADs with the coverage adjusted to take account of actual qty of points
Note on G76: Simon: This is the coverage of VADs with the coverage adjusted to take account of actual qty of points
Note on L82: Simon: True if standard power is availablre for ceiling
Note on C88: Simon: shows low output for HPW device if the Standard unit is not selected

## Roomsummary (hidden)
S-Quad Visual Alarm Estimate Summary
2015-03-20
Room ID | Room Name | Preferred Detector /Sounder Spacing | VAD Spacing | Ambient Light | Device Colour | Line of Sight | Part Ref | part Desc | Quantity | Length | Width | Ceiling Height | mounting Height | Device setting | Certified Category | Corrected coverage | *** Max Mounting Height | *** Max Spacing of VAD
0 | Room 1 | N/A | N/A | 150 | White | N/A | S3-S-VAD-HPR-R | S3 Sndr/High Perf Red VAD/Red Body | Not Set | 10 | 5 | 2.5 | Not Set | White / Low Power | Not Set | Not Set | Not Set | Not Set
0
|  | N/A | [12 empty] | W-3-8.5 | C - 9.6 - 25.9
Note on C11: Simon: Preferred Spacing