SECTION 28 23 00

VIDEO SECURITY SURVEILLANCE MANAGEMENT SYSTEM

Display hidden notes to specifier. (Don't know how? Click Here)

Copyright 2014 - 2021 ARCAT, Inc. - All rights reserved

** NOTE TO SPECIFIER ** Honeywell Commercial Security; security and automation solutions, video security surveillance management system. 
This section is based on the products of Honeywell Commercial Security, which is located at: 
715 Peachtree St. N.E. 
Atlanta, GA 30308 
Toll Free Tel: 800-323-4576 
Email:Shellie.Redden@Honeywell.com 
Web:https://buildings.honeywell.com/us/en/brands/our-brands/security 
[Click Here] for additional information. 
 
PART 1 - GENERAL

  - SECTION INCLUDES

    - Video surveillance and management system

      - Video Management System (VMS).

      - Network Video Recorders (NVR).

      - Embedded Video Recorders

      - NDAA Compliant Cameras

## RELATED SECTIONS

    - Section 16050 - Basic Electrical Materials and Methods.

    - Section 16100 - Wiring Methods.

    - Section 16700 - Communications.

  - REFERENCES

    - Canadian ICES-003.

    - Canadian Standards Association (CSA).

    - Consultative Committee for International Radio (CCIR).

    - Conformity for Europe (CE).

    - Electronic Industry Association (EIA).

    - Federal Communications Commission (FCC).

    - Institute of Electronic and Electrical Engineers (IEEE).

    - IP Code (Ingress Protection Rating) per IEC 60529.

    - Joint Photographic Experts Group (JPEG).

    - National Television Systems Committee (NTSC).

    - National Defense Authorization Act (NDAA)

    - Phase Alternating Line (PAL).

    - Underwriters Laboratories Inc. (UL).

    - Moving Pictures Experts Group (MPEG)

    - Motion Joint Photographic Experts Group (MJPEG)

    - ITU-T Video Coding Experts Group (VCEG)

    - Physical Security Interoperability Alliance (PSIA)

    - Open Network Video Interface Forum (ONVIF)

    - Real Time Streaming Protocol (RTSP)

  - DEFINITIONS

    - HD (High-definition) - refers to video having resolution substantially higher than traditional television systems. HD has one or two million pixels per frame.

    - CIF (Common Intermediate Format) - refers to a standard video format, which is categorized based on the resolution.

  - SUBMITTALS

    - General: Submittals shall be made in accordance with the Conditions of the Contract and Submittal Procedure Section 01300.

    - Manufacturer's Product Data: Manufacturer's data sheets indicating systems and components proposed for use, including instruction manuals.

    - Shop Drawings: Complete shop drawings including connection diagrams for interfacing equipment, list of connected equipment, and locations for major equipment components.

    - Record Drawings: During construction maintain record drawings indicating location of equipment and wiring. Submit an electronic version of record drawings not later than Substantial Completion of the project.

    - Operation and Maintenance Data: Manufacturer's operation and maintenance data, customized to the system installed. Include system and operator manuals.

    - Field Tests: Results of field testing of every device including date, testing personnel, retesting date (if applicable), and confirmation that every device passed field testing.

    - Maintenance Service Agreement: Sample copy of the manufacturer's maintenance service agreement, including cost and services for a one-year period for Owner's review. Maintenance includes, but is not limited to, labor and materials to repair systems, tests and adjustments, and regular inspections.

    - Verification Samples: For each finish product specified, two samples, minimum size 6 inches (150 mm) square representing actual product, color, and patterns.

  - QUALITY ASSURANCE

    - Manufacturer: Minimum of ten years' experience in manufacturing and maintaining video management systems. The manufacturer shall provide toll-free technical assistance and support available 24/7.

      - Customer service, pre-sales applications assistance, after-sales technical assistance, access to online technical support, and online training using Web conferencing.

      - The manufacturer shall provide 24/7 technical assistance and support by means of a toll-free telephone number at no extra charge.

    - Manufacturing Location:  Provide equipment assembled in the United States.

    - Installer: Minimum two years' experience installing similar systems, and acceptable to the manufacturer of the video management system.

    - Power Requirements: Components shall have the following electrical specifications: 100-240 V AC (50 Hz/60 Hz) or as specified for individual products within part 2 of the specification.

    - Mock-Up: Provide a mock-up for evaluation of surface preparation techniques and application workmanship.

      - Finish areas designated by Architect.

      - Do not proceed with remaining work until workmanship is approved by the Architect.

      - Rebuild mock-up area as required to produce acceptable work.

  - PRE-INSTALLATION MEETINGS

    - Convene minimum two weeks prior to starting work of this section.

  - DELIVERY, STORAGE, AND HANDLING

    - Deliver and store products in manufacturer's unopened packaging bearing the brand name and manufacturer's identification until ready for installation.

    - Handling: Handle materials to avoid damage.

  - PROJECT CONDITIONS

    - Maintain environmental conditions (temperature, humidity, and ventilation) within limits recommended by manufacturer for optimum results. Do not install products under environmental conditions outside manufacturer's recommended limits.

  - SEQUENCING

    - Ensure that products of this section are supplied to affected trades in time to prevent interruption of construction progress.

  - WARRANTY

    - Manufacturer's Warranty: Submit manufacturer's standard warranty for the video surveillance system.

- PART 2 - PRODUCTS

  - MANUFACTURERS

    - Acceptable Manufacturer: Honeywell Commercial Security, which is located at: 715 Peachtree St. N.E.; Atlanta, GA 30308; Toll Free Tel: 800-323-4576;

Email: Shellie.Redden@Honeywell.com

Website: https://buildings.honeywell.com/us/en/brands/our-brands/security

    - Substitutions: Not permitted.

      - Requests for substitutions will be considered in accordance with provisions of Section 01 60 00.

NOTE TO SPECIFIER: Delete if VMS is not required.

### SYSTEM DESCRIPTION

### Video Management System - Software, Client License, Server and Workstations

### The Video Management System (VMS) shall control multiple sources of video surveillance subsystems in a facility to collect, manage and present video in a clear and concise manner. VMS shall intelligently determine the capabilities of each subsystem across a single or multiple sites, allowing video management of any compatible analog or digital video device through a unified configuration platform and viewer.

  - OPERATIONAL REQUIREMENTS

    - VMS shall provide a single graphical user interface (GUI) to monitor, control and administer digital video surveillance equipment from multiple systems and platforms.

    - VMS shall include a fully scalable enterprise-class media management system to enable simultaneous live monitoring from multiple stations and be configurable for storage both on and off site.

    - VMS software shall be configured to store and to view images captured by one camera or numerous cameras and monitor connections across an unlimited number of servers.

    - The VMS application shall have following major capabilities:

      - Managing pentaplex user operations of attached recording devices simultaneously, including live viewing, recording, playback, archiving of video data to an external storage device, and handling the exchange of data between the server and a remote workstation.

      - Live viewing of up to 64 cameras on a single workstation with up to four monitors set up at CIF resolution. For 1080p and up to 4K resolution, the number of live streams shall be benchmarked based on the client hardware configuration deployed.

      - Integration with multiple digital and network video recording devices.

      - Integration with multiple video matrix switchers and matrix keyboards.

      - The number of recorders and switchers shall be scalable within a network to handle any size of installation.

      - Managing integration with multiple digital IP cameras through compatible recording devices.

      - Integration with electronic access control systems.

      - Integration with video analytics and a data management utility.

      - Managing failover and redundant capabilities of the recording device(s) and the database server. 1+1/N+M MAXPRO NVR failover and failback automatically or manually. View and playback on one client panel.

      - Managing investigation and video archive search tools of the recording devices.

      - Advanced search capabilities of the recording devices.

      - Managing motion detection-based recording.

      - Multi-level user access rights for managing viewing rights and access to the recorder functions.

      - Continuous, scheduled, manual, event-based and alarm-based recording features of the recording devices.

      - Support for Unicast network topologies and communication protocols.

      - Macro capability to allow for custom scripts and to provide both customization and third-party integration.

      - Honeywell Video Analytics integration

      - Support for both centralized and distributed architectures.

      - Simultaneous use of multiple video compression including H.264, H.265 (including camera dependent smart codec support), MPEG-4 and MJPEG.

      - Utilization of off-the-shelf computer workstations, servers, networking and storage equipment.

      - Person anonymization for GDPR compliance.

      - Support web client that supports modern web browser like Google Chrome, Microsoft Edge for:

        - View live, playback and control PTZ for one or more cameras from a single browser instance

        - Support setting stream preferences allows configuring either same stream as thick clients or a lower or higher quality video stream for web clients to cater to remote web clients

      - Shall support two-way audio integration with IP cameras

    - Cyber Security Features:

      - Enhanced password security – non-recoverable passwords, enforcing complex passwords, password expiry, and no default passwords.

      - Addressed Unauthenticated/Unauthorized channels.

      - Secured firewall configuration.

      - Secured Web client – enabled HTTPS and TLS 1.2, and protection from CSRF and XSS attacks.

      - Restricted folder and Registry access to operators.

      - Secured Assemblies – Digital signing.

      - Secure communication with the equIP Cameras using Honeywell proprietary protocol and Encrypted video streams with 30 Series, 35 Series, 60 Series, and 70 Series cameras using TLS 1.2

    - Mode for User Login:  VMS Server and Workstation shall have the option of two modes of user logins:

      - Windows Authentication: Uses the Windows logged-in username.

      - User DB Authentication: Uses a preconfigured username and password.

    - VMS Workstation shall provide the following operator functions:

      - Configuration: The operator (with Administrator privileges) shall have the option to configure VMS. VMS shall support live updates of all configurations. The following configurations shall be possible:

      - Recorders Configuration: Option to add/edit/delete recorders.

      - Camera Configuration: Option to add/edit/delete cameras and associate them to a particular recorder or switcher and map to a particular site, partition or event group.

      - Monitor Configuration: Option to add/edit/delete monitors and map to a particular site, partition, event group or keyboard. It shall provide an option to add a digital monitor and associate it with a particular workstation. It shall provide an option to configure a digital monitor with a default salvo and startup in full screen. It shall provide an option to add an analog monitor and associate it with a particular switcher. Option to save a digital correction in the video input page.

      - Switcher Configuration: Option to add/edit/delete analog video switchers.

      - Keyboard Configuration: Option to add/edit/delete keyboard controllers.

      - User Management (Users and Roles): Option to add/edit/delete roles and associate to predefined privileges and then add/edit/delete users and associate users with roles. Option to associate permissions with salvo selection and tool bar buttons.

      - Administrators of the system should have the option to force logout users from workstation clients. If more than one instance of a client is running in a workstation, administrator should be allowed to force log out the user from all client instances of a workstation

      - Site Configuration: Option to add/edit/delete a site.

      - Workstation Configuration: Option to add/edit/delete a workstation.

      - Event Group Configuration: Option to add/edit/delete event groups. Support of bulk event association to enable/disable and adjust events for recorders and inputs in bulk.

      - Partition Configuration: Option to add/edit/delete partitions.

      - Sequence Configuration: Option to add/edit/delete scan sequences.

      - Intercept Key Configuration: Option to add/edit/delete intercept keys from UltraKey keyboards to change the key function to a new and desired function.

      - System Macro Configuration: Option to add/edit/delete macros. Option to restore macros. Execute button option to trigger selected macros provides mechanism for testing written macros.

      - Port Configuration: Option to add/edit/delete keyboard controllers and analog video switchers to the ports available on the controller.

      - Viewer:

        - Capable of being launched multiple times on the same workstation a minimum of four (4) times to display four (4) viewers on four (4) separate monitors per workstation.

        - Main video viewing screen capable of showing 1x1, 2x2, 3x3, 4x4, 5x5, 6x6 1x5, 2x8, and 1x12 salvos of live or recorded video. The Viewer application shall be capable of a full screen mode where only the video salvo is displayed.

        - Each Viewer has the capability to be associated to a specific monitor on a workstation and be assigned a unique output number that is either selectable from the viewer device tree, an UltraKey controller, or from a system macro.

        - Capable of saving current salvo as a View and allowing the user to select the saved view by either dragging and dropping it into the viewer, using an UltraKey controller or a system macro.

        - Capable of selecting a particular camera or salvo by using the mouse to drag it onto the main video viewing screen. Users shall also have an undo/redo option for camera drag/drop and salvo selection from the viewer and UltraKey controller.

        - Capable of switching an analog camera to an analog or digital monitor so that the system will recognize to switch to the analog matrix switch or to pull the video from an encoder.

        - Capable of choosing My Salvos (unique to the current operator) or Shared Salvos while saving a salvo.

        - Capable of allowing duplicate salvo names to be set by different users and in different locations.

        - Capable of dragging any monitor defined in the system onto a video panel and taking control of that monitor.

        - Option to send a command to the controller to switch a particular analog camera onto the analog monitor through a drag and drop operation.

        - Capable of configuring and running scan sequences.

        - Capable of independently adjusting the contrast, brightness, and saturation settings for each camera.

        - Support for both analog and digital PTZs through the GUI or the keyboard.

        - Innovative “One-Click” or “Mouse Drag” 3D PTZ control experience that does away with legacy PTZ controls of continuous clicking.

        - Intelligence events from cameras can be viewed at the alarm panel and trigger event recording on MAXPRO NVRs for further investigation.

        - 360° de-warping “spreads” the distorted fisheye image into natural panoramic and/or multiple tile views. Operators can view and focus on zones of interest on live and recorded video.

        - Capable of exporting user selected images or video clips. A digital signature shall be attached to every exported clip.

        - Clip Creation: The Clip Creation facility shall permit multi-camera clip generation.

        - Story clips allow for selecting multiple cameras at different times to create a single clip to play the cameras back in order. Also supports saving salvo information in a story clip.

        - Salvo clips provide an instant clip export button to create an instant clip while maintaining the salvo information. Supports pre-determined pre- and post-times that are user-configurable in the preferences.

        - Clip preview window facility supports play back of the individual cameras prior to commencing clip creation.

        - Capable of manually setting the clip duration in the clip creation window for each camera.

        - Capable of playing back the exported video clips. Each video channel that is being recorded by the recording system shall be overlaid with text and a time stamp that is customizable by the user.

        - Allows the user to initiate recording through the GUI or controller.

        - Capable of complete alarm management for the alarms coming from recorders or switchers.

        - Quick and responsive alarm actions can be initiated from the preview pane options.

        - Application launch pad launches other applications from within the Viewer.

        - Control of operator messaging, allowing operators to communicate with each other. Operators can exchange text, images and annotated video sources. Operators can hand over a video source to another operator using messaging.

        - Ability to set up surrounding camera views. Support for setting presets in surrounding cameras.

        - Option to perform various operations through the context menu on a particular video (live/recorded/sequence). These operations include  Full screen, point and drag, enable square select, maintain aspect ratio, toggle text, digital PTZ, add bookmark, send message, start recording, stop recording, mark in, mark out, save image, save image as, and show surrounding cameras.

        - Ability to manage the timeline control of the recording device, which provides camera recording statistics. Timeline control shall have the following features: Mark in/out (with looping facility), bookmark (including for all playing cameras or all selected cameras or removing all bookmarks), snapshot, time slider, time search, time jump, and play controls. Timeline control shall also include dedicated buttons for step reverse and step forward and keyboard shortcuts for playback operations.

        - Support for bookmark searches based on cameras, time duration, and comments.

        - Controllable by a keyboard controller connected to the VMS server/controller with the following major features: selecting salvos, ending monitor commands, switching operations, and PTZ control operations.

        - Preference configuration including  fps of unselected panels, rendered type, preview pane, and text display format.

        - Support for smooth reverse playback at 2x (Recorder Dependent)

        - Capable of displaying analytics annotations (Recorder/Camera Dependent)

      - Search: The Search facility shall include searches based on date and time.

      - Reports:  The Report facility shall include event history reports and audit log reports.

      - Remote Monitor: The Remote Monitor facility shall allow operators to control a remote monitor connected to another workstation and perform review capabilities so that both the local operator and the remote viewer can simultaneously watch the same video.

      - Analytics Tab: Empowers visualizing all the scanned and recognized objects by various analytics algorithms across different cameras. This tab empowers the operators to visualize the people and vehicles appearances in a chronological order along with the properties for e.g., blacklisted, whitelisted. Analytics tab increases situational awareness by showing history trail of appearances of a vehicle or a person, validation through an instant recording playback through simple drag and drop of these events.    Crowd detection is another empowering analytic based on parameters set in the NVR for defining what constitutes as crowd and then providing proactive alarms when these specifications are reached.

    - Intelligent Command

      - The Intelligent Command Console is a suite consists a map-based user interface designed to improve situational awareness; Incident Workflow, designed to help standardize response and information recording for incidents and critical activities; Health Dashboard for displaying health status of devices at various level; Device Management for upgrading connected device firmware and changing passwords; Safety Compliance Dashboard to display the healthy safety metrics of a building such as number of social distancing violations, mask compliance violations and Recording Availability Dashboard for an active 24-hour view of cameras being recorded and confirming the number of days of historical activity for compliance.

      - Alarms:

        - System should support displaying the active and acknowledged alarms reported on the devices accessible to the logged in user

        - System should allow search and sorting based on the alarm fields

      - Maps:

        - The primary GUI (graphical user interface) is a high-resolution map with a deep zoom capability allowing easy navigation of the facility to find issues or to review areas of interest. Large-scale individual maps are linked with simple navigation to seamlessly access maps at national, local and site levels with building details and individual internal floorplans. Navigation on the maps is simple and intuitive, using pinch-to-zoom and drag-to-pan as commonly adopted on touch interfaces, and can also be operable with a mouse control if appropriate.

        - System should support configuring image-based maps (.jpg, .png, .bmp)

        - System should support configuring online GIS maps and should leverage OpenStreet maps

        - System should support importing the maps directly from CAD files

        - To aid navigation between maps and support the user in identifying issues, at each level there are links to lower-level maps. As an example, when viewing a map of a building there would be links to each floor within the building.

        - Camera ‘Smart Objects’ are represented on the maps by active ‘smart objects. These objects represent the cameras in the system, support showing the live video stream, options to playback and to PTZ operations.

        - To provide an uncluttered interface with immediate visibility of key equipment and information, the map will be configured to show a small selection of key smart objects when zoomed out, but for additional object to be progressively disclosed as the user zooms into specific areas of the map. During usual monitoring of the facility this enables the status of the cameras or doors to be monitored continuously while the user can zoom into particular areas when additional information is required.

        - To allow faster response time for operators, upon selecting one of the active alarms, the system should display the device location on a map and highlight the device on map. Additionally, the system should display history of alarms and the related live or recorded video all in one screen.

      - Incident Workflow:

        - Workflow Initiation:

          - The IW system contains standard operating procedures (SOPs) that are presented to the operator as a set of steps when a workflow is initiated. Workflows can be initiated automatically as a result of alarms or can be initiated manually by the operator (for example for crowd trouble). When a workflow is initiated manually, the operator is presented with a list of available SOPs through a display of user-friendly icons which makes selection quick and simple.  When creating an incident, the operator can add location and device name which is based on Hierarchy Builder information and provides full depiction and documentation regarding the event.

        - Workflow Execution:

          - An operator can take ownership of the workflow by pressing the ‘Respond’ button which enables the workflow buttons and allows the operator to check off each step when completed. When the operator marks a step as completed, the operator’s name (system log-in) and the time and date of the step being completed is recorded. Only the responding operator is able to check-off SOP steps at any one time.

          - The operator can release control of the SOP by navigating away from the display and then another operator can take control. Any logged-on operator is able to add comments to the SOP header or to individual steps facilitating team working and collaboration on the workflow while maintaining control and responsibility.

          - All comments and other actions are time-stamped and naming for full traceability. Comments are able be added to the workflow or to individual steps, and the name of the operator and the time and date of the comment’s entry is recorded.

      - Evidence attachments:

        - The system should allow the users to attach evidence such as documents and pictures to created incidents.

        - Other users having access to the incidents should be allowed to review the attached evidence

        - System should support generating a detailed report for incidents which includes the details of the incident attachments as well

        - System should securely store the attachments and at periodic intervals, should purge the evidence attachment to free up the diskspace

      - System Health Dashboards:

        - An integrated dashboard is provided featuring an efficient and effective means of visualizing system device health. Dashboard allows viewing status of system components such as recorders and their vital health metrics such as CPU usage, memory usage, available disk storage.  Recording timeline overview provides deep analysis into storage availability of Honeywell MAXPRO® NVR and Honeywell Pro-Watch NVR. Health dashboard also allows accessing status of individual cameras and allows to search by name and filter by various parameters

      - Device Management Console:

        - Empowers the users to carry out maintenance activities efficiently by knowing the current state vs recommended state. Device management console enables managing cameras by allowing system administrator to maintain a firmware inventory, view current firmware version vs installed version and initiate firmware upgrade simultaneously for all or selected cameras. In addition to firmware upgrades, the system lets administrators to easily comply with password management policies for peripheral devices by allowing the camera password simultaneously for all or selected cameras.

      - Safety Compliance Dashboard:

        - Envisages the compliance violation issues and adherence levels of a facility with respect to safety compliance protocols set by customer’s organization. Safety compliance dashboard contemplates the overall safety levels of a building by graphically displaying occupancy levels with a drill down option to view details of each metric for e.g.  number of compliance issues detected such as social distancing violations or non-observance of mask guidelines.

      - Video salvo views:

        - System should allow configuring video salvos to be used in intelligent command. Support salvo layouts include but not limited to 1x2, 2x2, 3x3

        - System should support displaying live and playback, controlling PTZ in the web client

        - Intelligent Command web client should support modern web browser like Chrome, Edge, Mozilla Firefox and Safari to view cameras configured with codecs H.264 and H.265

    - Mobile App:

      - VMS and Intelligent Command should support mobile app for Android® and iOS® platforms

      - Mobile app should support viewing live, recorded videos, controlling PTZ and responding to alarms

      - Communication between the server and the mobile app should be encrypted for both video and non-video data

#### VMS INTEGRATIONS

      - Recorders:  
VMS shall support integration with digital and network video recorders (DVRs/NVRs). VMS shall have the ability to access and manage necessary functions of the recording devices through the VMS client interface, such as live video, recorded video, camera configuration, PTZ control and other associated functions. The system shall support the following recording devices:

        - Honeywell MAXPRO® NVR

        - Honeywell Pro-Watch NVR

        - Honeywell ADPRO iFT Series NVR and Gateway

        - Honeywell Performance Series NVR

        - Honeywell 35 Series NVR

        - 3rd Party recorder integrations such as Avigilon NVR

      - Analog Video Switchers: 
VMS shall support matrix switcher integration including camera call up, monitor switching, video command support and PTZ support. The video subsystem shall be the controller device for video cameras, monitors, and VCRs, and shall associate camera inputs with monitor outputs. The system shall allow users to program video monitors and video cameras to execute commands upon recognition of an alarm or any other condition within the system. The user shall be able to add, edit, delete, and partition video subsystems. The system shall support the following analog video switchers:

        - Honeywell VideoBloX Series

        - Ultrak MAXPRO-1000

        - Pelco 9600 Series

        - American Dynamics

        - Vicon

        - Burle

      - Video Analytics:

        - Honeywell Active Alert

        - IntrusionTrace and LoiterTrace of ADPRO NVR

        - Intrusion, Loiter, Line Cross, Face Detection, Object Left, Object Removed, Smart Motion, Tamper, License Plate Recognition with Honeywell 70 Series IP cameras with MAXPRO NVR

        - Allgovision analytics

        - Idemia analytics

        - Ipsotek analytics

        - Mask Detection, Social Distance, and Crowd Detection with MAXPRO NVR

      - Data Management Utility:   Honeywell Integrated Data Manager

      - IP Surveillance Control Keyboards:  Honeywell HJK7000 UltraKey Plus

      - Electronic Access Control Systems:  Honeywell Pro-Watch Release 3.8 or later

#### SYSTEM HARDWARE

    - VMS Server:

      - Server shall operate with no performance degradation using the following minimum hardware and operating system configuration:

      - Processor:

        - Up to 5 Client Server:  Single Intel® Quad Core Xeon® E3 1225V3 3.2 GHz S1150

        - Up to 10 Client Server:  Single Intel® Quad Core Xeon® E-2134 3.5GHz

        - Up to 25 Client Server:  Dual Intel® 8 Core Xeon® Silver 4110 2.1 GHz

      - System Memory (RAM):

        - Up to 5 Client Server:  8 GB

        - Up to 10 Client Server:  16 GB

        - Up to 25 Client Server:  32 GB

      - Optical Drive:  DVD+/-RW

      - Hard Disk Drives: Two separate hard drives or two sets of RAID arrays.

        - Disk/RAID set 1 utilizing 7200 SATA or 10K-15K RPM SCSI 146 GB

        - Disk/RAID set 2 utilizing 7200 SATA or 10K-15K RPM SCSI 146 GB

        - If fault tolerance is required, RAID set one is RAID 1 or 10 and RAID set two is RAID 10 or 0 + 1

      - Network Interface Card (NIC):  Dual or compatible pair of NICs, 1 Gbps

      - Human Interface:  102-key keyboard and a mouse pointing device

      - Graphics Adapter:  32-bit color or higher, video resolution 1280x1024 pixels, 65K colors non-interlaced

      - Operating System:  Original software CDs and startup installation diskettes for:

        - Windows® Server 2008 R2 Standard SP1 64-bit OR Windows Server 2012 Standard 64-bit OR Windows Server 2016 R2

        - Microsoft SQL Express 2008 R2 OR SQL Express 2012

      - Windows Media Player Version 12

      - For installations where the system is integrated with Honeywell IP Engine recording software with more than 500 cameras, install a separate IP Engine database server. The specification of this server shall be determined based on end-user deployment requirements.

NOTE TO SPECIFIER:  Workstation configuration can use either a two (2) or four (4) monitor setup.  Select the workstation configuration for the monitor setup that is required.

    - VMS Dual or Quad Monitor Workstation:

      - Workstation shall operate with no performance degradation using the following minimum hardware and operating system configuration for a two (2) monitor setup or four (4) monitor setup:

        - Processor:  Intel® Core™ i7-8700, 3.2 GHz or equivalent newer generation Intel® Core™ Processors for client systems.

        - System Memory (RAM): 16 GB

        - Optical Drive:  DVD-RW

        - Hard Disk Drives:  Single disk or RAID 7200 SATA 250 GB or 10K to 15K SCSI 250 GB; RAID 0 or 0+1.

        - Network Interface Card (NIC):  1 Gbps

        - Human Interface:  102-key keyboard and a mouse pointing device

      - Graphics Adapter:

        - [four monitor setup]: Integrated Intel UHD graphics 630 and NVIDIA Quadro P620

        - [two monitor setup]: Integrated Intel UHD graphics 630

        - Operating System:  Windows 7 Professional or Windows 10 Enterprise, 64-bit Windows Media Player Version 12

#### WARRANTY

      - Manufacturer’s Guarantee:  Standard one (1) -year warranty for the video surveillance system

NOTE TO SPECIFIER: Delete if MAXPRO NVRS are not required.

  - SYSTEM DESCRIPTION

    - MAXPRO® Network Video Recorders

      - The Network Video Recorder (NVR) supports simultaneous recording, remote viewing and search, and system management for up to 128 IP cameras including high-definition formats based on specific model. Multiple NVRs may be deployed for system expansion using a distributed architecture and integrated with the multi-site software or enterprise video management system.

      - NVR Server: The NVR Server shall contain the recording engine, database of all network-connected cameras and encoders, integrated components, and their configurations. Server shall be provided as a combined hardware and software device.

      - Workstation Software (NVR Client): The NVR Client software shall render video and act as a main human/machine interface.

  - OPERATIONAL REQUIREMENTS

    - NVR shall provide a user-friendly graphical user interface (GUI) to configure the cameras, create schedules for recording, perform video surveillance and recording operations, and view various reports.

    - NVR shall be configured to store and to view images captured by up to 128 cameras depending on model listed below:

      - PE (PROFESSIONAL EDITION) NVR shall have following major capabilities:

        - Record and monitor up to 128 IP channels at 3840 fps @ 4CIF/VGA or 3840 fps @ 720p HD or 3840 fps @ 1080p (4 Mbps bitrate) HD per MAXPRO NVR PE. Network bandwidth/throughput supported per NVR with Incoming: 530 Mbps, Outgoing: 270 Mbps providing a Total: 800 Mbps. Archival support of 25 channels @ 4 Mbps bitrate each (100 Mbps total archival throughput capacity per MAXPRO NVR PE), with outgoing archival storage throughput of 275 Mbps. Multi-stream support with maximum 256 streams per MAXPRO NVR PE. Support for configuring one (1) preferred stream for continuous recording and one (1) preferred stream for live video/motion based recording per camera. Support for One-Way Audio (for specific IP cameras) with live, playback and clip export on NVR desktop client for up to 128 IP channels.

        - Live viewing of up to 64 IP cameras on a single remote workstation with up to two (2) monitors set up at CIF resolution. For 4CIF and HD resolution, the number of live streams needs to be benchmarked based on client hardware configuration deployed. Cost-effective enhanced HD video rendering on remote desktop clients with support for monitoring of up to 23 1080p HD cameras in real time (30 fps)/690 fps 1080p HD with no-time lapse using the GPU capabilities of in-built processor graphics with Intel® Core™ Processors for client systems. Up to 4 1080p HD @ 30 fps/120 fps on local client.

      - SE (STANDARD EDITION) NVR shall have the major capabilities:

        - Record and monitor up to 64 IP channels at 1920 fps @ 4CIF/VGA or 1920 fps @ 720p HD or 1280 fps @ 1080p (4 Mbps bitrate) HD per MAXPRO NVR SE. Network bandwidth/throughput supported per NVR with Incoming: 160 Mbps, Outgoing: 280 Mbps providing a total: 440 Mbps. Archival support of 16 channels @ 4 Mbps bitrate each (64 Mbps total archival throughput capacity per MAXPRO NVR SE), with outgoing archival storage throughput of 200 Mbps. Multi-stream support with maximum 128 streams per MAXPRO NVR SE. Support for configuring one (1) preferred stream for continuous recording and one (1) preferred stream for live video/motion based recording per camera. Support for One-Way Audio (for specific IP cameras) with live, playback and clip export on NVR desktop client for up to 64 IP channels.

        - Live viewing of up to 64 IP cameras on a single remote workstation with up to two (2) monitors set up at CIF resolution. For 4CIF and HD resolution, the number of live streams needs to be benchmarked based on client hardware configuration deployed. Cost-effective enhanced HD video rendering on remote desktop clients with support for monitoring of up to 23 1080p HD cameras in real time (30 fps)/690 fps 1080p HD with no-time lapse using the GPU capabilities of in-built processor graphics with Intel® Core™ Processors for client systems. Up to 4 1080p HD @ 20 fps/80 fps on local client.

      - XE (XPRESS EDITION) NVR shall have the major capabilities:

        - Record and monitor up to 16 IP channels at 480 fps @ 4CIF/VGA or 480 fps @ 720p HD or 480 fps @ 1080p (4 Mbps bitrate) HD per MAXPRO NVR XE. Network bandwidth/throughput supported per NVR with Incoming: 80 Mbps, Outgoing: 240 Mbps providing a Total: 320 Mbps. Archival support of 16 channels @ 4 Mbps bitrate each (64 Mbps total archival throughput capacity per MAXPRO NVR XE), with outgoing archival storage throughput of 200 Mbps. Multi-stream support with maximum 128 streams per MAXPRO NVR XE. Support for configuring one (1) preferred stream for continuous recording and one (1) preferred stream for live video/motion-based recording per camera. Support for One-Way Audio (for specific IP cameras) with live, playback and clip export on NVR desktop client for up to 8 or 16 IP channels.

        - Live viewing of up to 16 IP cameras on a single remote workstation with up to two (2) monitors set up at CIF resolution. For 4CIF and HD resolution, the number of live streams needs to be benchmarked based on client hardware configuration deployed. Cost-effective enhanced HD video rendering on remote desktop clients with support for monitoring of up to 23 1080p HD cameras in real time (30 fps)/690 fps 1080p HD with no-time lapse using the GPU capabilities of in-built processor graphics with Intel® Core™ Processors for client systems. Up to 4 1080p HD @ 30 fps/120 fps on local client.

    - NVR shall have the following major capabilities:

      - Support audio configuration to be set for individual cameras. Additionally, system should enable selecting the direction of the audio stream flow: Only audio-in, only audio-out or both (PE model)

      - Powerful investigation and video archive search tools from remote client.

      - Native device integrations supporting cameras’ features: 4K resolution, H.265 video compression codec, 3D PTZ control, 360° camera support, and intelligence events.

      - Native device integrations supporting Honeywell 30 Series and 60 Series cameras’ new features: H.265 smart video compression codec and encrypted video stream with TLS 1.2

      - Capable of managing motion detection-based recording with pre-event and post-event recording based on camera-based motion detection or Server based motion detection events (SMART VMD) and “advanced” search on recordings from remote client. (SMART VMD is not recommended when more than 64 cameras are connected to the NVR.)

      - Preview and Calendar Search permitting search for videos and events based on user-selected date and time from remote client. SMART motion search — fast and efficient forensic search and investigation for objects/motion on recorded video using Honeywell SMART motion detection Analytics algorithms on the client PC without impacting the NVR Server load.

      - Simultaneous use of multiple video compressions including MJPEG, MPEG-4, H.265 and H.264.

      - Languages: French, German, Russian, Italian, Spanish, Dutch, Arabic and English.

      - Email on alarm.

      - Instant clip creation from snapshot.

      - Dynamic IP Camera Discovery – Automatically discover all compatible cameras connected to NVR.

      - Multi-level user access rights for viewing and manages access to the recorder functions.

      - Capable of managing continuous, scheduled, manual, event-based, and alarm-based recording features.

      - Advanced security features with encryption support for communication between desktop client to NVR and secure https login for Web Client and mobile apps.

      - Support for web clients and mobile apps.

      - Capable of person anonymization for GDPR compliance.

      - Capable of displaying analytics annotations (Camera Dependent).

    - Mode for User Login:  NVR shall have the option of two modes of user logins:

      - Windows Authentication: Uses Windows logged-in username.

      - User DB Authentication: Uses preconfigured username and password.

    - Workstation (NVR Client) shall provide the following operator options:

      - Configuration: The operator (with Administrator privileges) shall have the option to configure the NVR. Live update of all configurations is supported. The following configurations shall be possible:

        - System Configuration: Provide options to configure the system level settings.

        - Camera Configuration: Provide options to add/edit/delete IP cameras and encoders.

        - Schedules: Provide options to configure schedule-based recording for cameras connected to the NVR.

        - Input and Output: Provide options to configure camera input and output.

        - Sequences: Provide options to group a fixed number of cameras to view video.

        - User Management (Users and Roles): Provide option to add/edit/delete users.

        - Clip Deletion Settings: Provide the ability to automatically utilize more storage on event-initiated recording.

        - Independent deletion setting for continuous recording.

        - Independent deletion setting for event recording.

        - Surrounding Cameras: Provide option to grant a user the ability to view a single camera surrounded by the cameras programmed as the “Surrounding Cameras”.

        - 3D Positioning: The user shall be able to view a specific object in the live video in a 3-dimensional view.

        - Profile Cameras: Multi-zoom views on HD video and support to create virtual cameras by digitally zooming into the field of view.

    - Configurations for cameras connected to NVR:

      - Camera Configuration: The user shall be able to configure the following parameters for each camera connected to the NVR.

        - Camera Name

        - IP Address

        - Camera Type

        - Fixed/PTZ

        - Continuous Recording: All cameras added shall be defaulted to "24/7" recording with the option to select other recording modes.

        - Event Based Recording: Shall be “None” by default, with the option to select motion-based recording.

        - Username: Shall display and enable setting the username for a camera.

        - Password: Shall enable setting the password for a camera.

        - Camera Advanced Settings:  Shall enable configuration of Video Format, Compression Format, Resolution, Compression, Video Frame Rate, GOP, Record Quality Settings, Clip Deletion Settings, Launching Web View of camera for Advanced Setup, Motion detection zones configuration for Server based motion detection, Video Archival Settings, Multi-Stream Settings, and Video Preview. Shall enable configuration of RTSP URL for cameras or encoders added with camera type – Generic RTSP.

      - The following video recording options shall be supported:

        - Scheduled based recording: The system shall support the ability to schedule recordings for each individual camera for times in the future. By default, the NVR shall be pre-loaded with the following four schedules: 24x7, Weekday, Daytime, and Nighttime, which cannot be edited. A maximum of 50 schedules can be created in the NVR.

        - User based recording: The user shall be able to configure user activated settings for recording moments of interest while viewing live video from a camera. After configuring the user activated settings, the operator can start recording video when needed. The video is recorded for the time period specified in the System settings for user activated recording. The User based Recording Time Duration shall be selectable from a list of values ranging between 30 seconds and 5 minutes.

        - Event based recording: Event based recording shall be possible on SMART Video Motion Detection and alarm triggers. The NVR must be capable of managing motion detection-based recording with pre-event and post event recording based on camera and Server-based motion detection events. The server-based SMART VMD analytics must be object-based and not traditional pixel-based, reducing false alarms due to changing light conditions, video noise, rain or other false alarm triggers that occur using pixel-based (traditional) VMD.

      - System supports efficient camera configuration and modifications by enabling to set below properties at bulk

        - Video stream configurations

        - Device type

        - Device environment

        - Recording retention details

        - Server side VMD (Video Motion Detection) settings

    - Viewer:  The NVR Viewer shall have the following minimum capabilities:

      - Main video viewing screen capable of showing 1, 4, 9, 16, and other customized split salvos of live or recorded video. Standard presets shall be customizable to the user preferences.

      - Capable of saving current salvo as a View and letting the user drag this view later.

      - Capable of configuring and running scan sequences.

      - Capable of adjusting the contrast, brightness, and saturation settings for each camera independently.

      - Capable of exporting user selected image or video clips in simple .wmv, .asf, .mpvc and .bmp formats. Capable of attaching a digital signature for authentication of exported clips in .wmv format.

      - Capability to play back the video clips exported. Each video channel that is being recorded by the recording system shall be overlaid with text and a time stamp that is customizable by the user.

      - MAXPRO Video Container (.mpvc) format support — only playable in MAXPRO desktop clients and standalone Clip Player. Features quicker exports of raw video and support for estimating clip size and split to multiple clips to ensure clip storage media matches. Include the clip player with exported clip for easier review of video evidence and efficient investigation. Clip Player — Portable standard secure player for archived and exported clips (*.mpvc), 360 camera de-warping and 2x2 Salvo support. Smooth playback support with up to 256x review speed. No software needed to run on a Windows PC, with the option to include the clip player with the exported clip.

      - Allow the user to initiate recording through the GUI or a controller.

      - Capability of complete alarm management for the alarms coming from the NVR.

      - Facility of surrounding camera view.

      - Option to perform various operations through context menu on a particular video (live/recorded/sequence). These operations include:  Full screen, point and drag, maintain aspect ratio, toggle text, digital PTZ, add bookmark, start recording, stop recording,	 mark in, mark out, save image, save image as, show surrounding cameras.

      - Ability to manage timeline control of the recording device, which provides camera recording statistics. Timeline control shall have the following features: Mark input (with looping facility), bookmark, snapshot, time slider, time jump, play controls.

      - Preference configuration including:  frame rate of unselected panels, rendered type, preview pane, text display format.

    - Search:  The Search facility shall include search for recorded video and events based on date and time.

    - Reports:  The Report facility shall include event history report and audit log report.

  - NVR INTEGRATIONS 
A.    NVR shall be compatible with the following interoperability standards:

      - Physical Security Interoperability Alliance (PSIA)

      - Open Network Video Interface Forum Profile S (ONVIF Profile S)

      - Real Time Streaming Protocol (RTSP)

    - NVR Supports IP cameras from the following manufacturers. Please contact Honeywell for the complete list of manufacturers and models.

      - AXIS® Communications

      - Sony

      - Panasonic

      - Bosch

      - Samsung

      - Vivotek

      - Pelco

    - NVR shall be compatible with the following encoders. Please contact Honeywell for the complete list of manufacturers and models.

      - AXIS® Communications

      - Sony

      - Panasonic

      - Bosch

      - Samsung

      - Vivotek

    - NVR shall be compatible with the following 360° Camera solutions. Please contact Honeywell for the complete list of models.

      - Honeywell 30 Series Fisheye IP Cameras

      - Oncam Grandeye

      - Immervision Enables® - Panomorph Lenses

      - AXIS® 360°/180°

      - Arecont 360°/180°

    - NVR shall be compatible with the Honeywell HJK7000 UltraKey Plus IP Surveillance Control Keyboard

    - NVR shall be compatible with the MAXPRO® Viewer Multi-site Video Management Systems

    - NVR shall be compatible with the MAXPRO® VMS Video Management Systems:

    - NVR shall be compatible with the following Access Control Security System:

      - Pro-Watch® Access Control System through MAXPRO® VMS and MAXPRO® Viewer

      - Honeywell WIN-PAK® Access Control System

    - Video Analytics supported:

      - Honeywell Active Alert through MAXPRO® VMS

      - VehicleTrace License Plate Recognition of HBL6GR2-LPR camera managed by MAXPRO VMS

NOTE TO SPECIFIER: Delete if PE NVR is not required.

NOTE TO SPECIFIER: MAXPRO NVR PE is provided as a single unit with preconfigured hardware and MAXPRO NVR software.  MAXPRO NVR software is also available separately for purchase and installation on COTS hardware.

  - SYSTEM HARDWARE

    - MAXPRO NVR PE Server:  NVR Server shall operate with no performance degradation using the following minimum hardware and operating system configuration:

      - 2U 12 bay storage unit with SATA hard drives

      - Processor:  Intel® Xeon® Silver 4110, 2.1 GHz

      - Memory: 16GB (32GB for 128 Channel)

      - Power supply: Dual redundant 750 W

      - OS Drives: 2 x 240 GB M.2 solid state drives, RAID 1 support

      - Operating system:  Windows 10 IoT Enterprise, 64-bit

      - Database:  Microsoft SQL Server Express 2012

      - Storage capacities:  16 TB to 144 TB raw storage, Video storage redundancy with RAID 5/6 support

      - Video Storage Hard Disk Options:  12 field-upgradable 4 TB, 8 TB, 10T or 12TB SATA Hard Disk Drive options

      - Optical drive:  None

      - Network interface:  Four 1 Gigabit Ethernet

      - RAID card:  6 GB SAS/SATA RAID card, PCI Express x8, supports RAID levels up to 6+0

      - Human Interface:  102-key keyboard and a mouse pointing device

      - Monitor Output:  2x VGA (1 monitor support)

      - Rack kit:  Rack kit for use with 2U chassis

    - NVR Workstation:

      - NVR Workstation shall operate with no performance degradation using the following recommended hardware and operating system configuration for rendering up to twenty-three (23) 1080p HD cameras in real time (30 fps)/690 fps @ 1080p HD with no time-lapse.

      - Workstation configuration assumes two-monitor setup.

      - Workstation is required for remote clients only; a local client is available on the NVR PE unit for configuration and monitoring. The performance specifications below are recommended for systems with fixed or PTZ cameras only. Oncam Grandeye 360 cameras are not supported with GPU rendering and use CPU rendering by default. On Windows 10 workstations with Intel GPU and any additional graphics cards, at least one monitor should be connected to the motherboard monitor output.

      - Processor:  Intel® Core™ i7-8700, 3.2 GHz or equivalent newer generation Intel® Core™ Processors for client systems.

      - Graphics Adapter: In-built Processor Graphics (GPU): Intel® HD Graphics 530, 4600 or equivalent.

      - System Memory (RAM):  16 GB

      - Optical Drive:  DVD-RW

      - Hard Disk Drives: Single Disk or RAID 0 or 0+1 10K SATA 80GB or 10K to 15K  
SAS 73 GB.

      - Network Interface Card (NIC):  1 Gbps

      - Human Interface:  102-key keyboard and a mouse pointing device

    - Operating System:  Microsoft® Windows 7 Professional 64-bit SP1, Windows 8.1 Professional 64-bit, or Windows 10 Professional 64-bit

  - ELECTRICAL REQUIREMENTS

    - The NVR shall have the following electrical specifications:

      - Input Voltage:  110/220 VAC 50/60 Hz

      - Operating Voltage:  110V/220V Auto Sensing

      - Power Dissipation:

      - Average BTU rating = 880 BTU/HR

      - Peak BTU rating = 2800 BTU/HR

  - ENVIRONMENTAL AND REGULATORY REQUIREMENTS

    - The NVR shall be designed to function in the following environmental conditions:

    - Operating Temperature:  50°F to 95°F (10°C to 35°C).

    - Emissions:  FCC part 15B Class A; EN 55022 Class A

    - Immunity:  EN 50130-4

    - Safety:  ANSI / UL 60950-1; CAN / CSA C22.2 No. 60950-1; IEC 60950-1.

    - RoHS: EN 50581.

  - WARRANTY

      - Manufacturer’s Guarantee: Five (5) years from the manufacture date code under normal use and service for the video surveillance system.

NOTE TO SPECIFIER: DELETE IF SE NVR is not required.

NOTE TO SPECIFIER: MAXPRO NVR SE is provided as a single unit with preconfigured hardware and MAXPRO NVR software.  MAXPRO NVR software is also available separately for purchase and installation on COTS hardware.

  - SYSTEM HARDWARE

    - MAXPRO NVR SE Server:  NVR Server shall operate with no performance degradation using the following minimum hardware and operating system configuration:

      - 2U 6 bay storage unit with SATA hard drives

      - Processor:  Intel®  Core™ i7-9700, up to 4.90 GHz, Intel® HD Graphics 630

      - Memory:  16 GB

      - Power supply:  Single 400 W

      - OS Drive:  250 GB M.2 SSD

      - Operating system:  Windows 10 IOT

      - Database:  Microsoft SQL Server Express 2019

      - Storage capacities:  4 TB to 60 TB with 6 bays

      - Video Storage Hard Disk Options:  6 field-upgradable 4 TB, 8 TB, 12 TB, or 16 TB SATA Hard Disk Drive options

      - Optical drive:  DVD-RW

      - Network interface:  Two 1 Gigabit Ethernet included

      - Human Interface:  102-key keyboard and a mouse pointing device

      - Monitor Output:  Dual monitor support: HDMI, VGA, DVI-D, Display Port

      - Rack kit:  Rack kit for use with 2U chassis

    - NVR Workstation:

      - NVR Workstation shall operate with no performance degradation using the following recommended hardware and operating system configuration for rendering up to twenty-three (23) 1080p HD cameras in real time (30 fps)/690 fps @ 1080p HD with no time-lapse.

      - Workstation configuration assumes two-monitor setup.

      - Workstation is required for remote clients only; a local client is available on the NVR SE unit for configuration and monitoring. The performance specifications below are recommended for systems with fixed or PTZ cameras only. On Windows 10 workstations with Intel GPU and any additional graphics cards, at least one monitor should be connected to the motherboard monitor output.

      - Processor:  Intel® Core™ i7-8700, 3.2 GHz or equivalent newer generation Intel® Core™ Processors for client systems.

      - Graphics Adapter:  In-built Processor Graphics (GPU):  Intel® HD Graphics 530, 4600 or equivalent.

      - System Memory (RAM):  16 GB

      - Optical Drive:  DVD-RW

      - Hard Disk Drives:  Single Disk or RAID 0 or 0+1 10K SATA 80GB or 10K to 15K  
SAS 73 GB.

      - Network Interface Card (NIC):  1 Gbps

      - Human Interface:  102-key keyboard and a mouse pointing device

      - Operating System:  Microsoft® Windows 7 Professional 64-bit SP1, Windows 8.1 Professional 64-bit, or Windows 10 Professional 64-bit

  - ELECTRICAL REQUIREMENTS

    - The NVR shall have the following electrical specifications:

      - Input Voltage:  110-240 VAC 50/60 Hz

      - Power Dissipation:

      - Average BTU rating = 569 BTU/HR

      - Peak BTU rating = 1370 BTU/HR

  - ENVIRONMENTAL AND REGULATORY REQUIREMENTS

    - The NVR shall be designed to function in the following environmental conditions:

      - Operating Temperature:  40°F to 104°F (5°C to 40°C).

      - Emissions:  FCC part 15B Class B.

      - Safety:  ANSI / Nemko (UL 62368-1 2nd Edition; CAN / CSA C22.2 No. 62368-1-14 (R2019)).

  - WARRANTY

    - Manufacturer’s Guarantee: The warranty period shall be thirty six (36) months from the delivery date of the system under normal use and service.

NOTE TO SPECIFIER: Delete if XE NVR is not required.

NOTE TO SPECIFIER: MAXPRO NVR XE is provided as a single unit with preconfigured hardware and MAXPRO NVR software.  MAXPRO NVR software is also available separately for purchase and installation on COTS hardware.

  - SYSTEM HARDWRE

    - MAXPRO NVR XE Server:  NVR Server shall operate with no performance degradation using the following minimum hardware and operating system configuration:

      - Desktop unit with internal SATA hard drives

      - Processor:  Intel® Core™ i5-9500 up to 4.40Ghz, Intel® HD Graphics 630

      - Memory:  8 GB

      - Power supply:  Single 300 W

      - OS Drive:  250 GB M.2 SSD

      - Operating system:  Windows 10 IOT, 64-bit

      - Database:  Microsoft SQL Server Express 2019

      - Storage capacities:  4 TB, 8 TB, 12 TB, 16TB, or 20 TB

      - Video Storage Hard Disk Options:  Internal fixed 2TB, 4 TB, 8 TB, 12TB or 16TB SATA Hard Disk Drive options

      - Optical drive:  DVD-RW

      - Network interface:  Two 1 Gigabit Ethernet included

      - Human Interface:  102-key keyboard and a mouse pointing device

      - Monitor Output:  HDMI, Display Port, DVI-D, or VGA

    - NVR Workstation:

      - NVR Workstation shall operate with no performance degradation using the following recommended hardware and operating system configuration for rendering up to twenty-three (23) 1080p HD cameras in real time (30 fps)/690 fps @ 1080p HD with no time-lapse.

      - Workstation configuration assumes two-monitor setup.

      - Workstation is required for remote clients only; a local client is available on the NVR XE unit for configuration and monitoring. The performance specifications below are recommended for systems with fixed or PTZ cameras only. On Windows 10 workstations with Intel GPU and any additional graphics cards, at least one monitor should be connected to the motherboard monitor output.

      - Processor:  Intel® Core™ i7-8700, 3.2 GHz or equivalent newer generation Intel® Core™ Processors for client systems.

      - Graphics Adapter:  In-built Processor Graphics (GPU):  Intel® HD Graphics 530, 4600 or equivalent.

      - System Memory (RAM):  8 GB

      - Optical Drive:  DVD-RW

      - Hard Disk Drives:  Single Disk or RAID 0 or 0+1 10K SATA 80GB or 10K to 15K  
SAS 73 GB.

      - Network Interface Card (NIC):  1 Gbps

      - Human Interface:  102-key keyboard and a mouse pointing device

      - Operating System:  Microsoft® Windows 7 Professional 64-bit SP1, Windows 8.1 Professional 64-bit, or Windows 10 Professional 64-bit.

  - ELECTRICAL REQUIREMENTS

    - NVR shall have the following electrical specifications:

      - Input Voltage:  115/230 VAC, 7/4 A, 60/50 Hz

      - Power Dissipation:

      - Average BTU rating = 320 BTU/HR

      - Peak BTU rating = 1030 BTU/HR

  - ENVIRONMENTAL AND REGULATORY REQUIREMENTSE

    - The NVR shall be designed to function in the following environmental conditions:

      - Operating Temperature:  40°F to 104°F (5°C to 40°C).

      - Emissions:  FCC part 15B Class A; EN55022:2010.

      - Safety:  ANSI / Nemko (UL 62368-1 2nd Edition; CAN / CSA C22.2 No. 62368-1-14 (R2019)).

  - WARRANTY

    - Manufacturer’s Warranty:  The warranty period shall be thirty six (36) months from the delivery date of the system under normal use and service

NOTE TO SPECIFIER: Delete if 35 Series recorders are not required

  - SYSTEM DESCRIPTION

    - Series 35 Network Video Recorders

      - Honeywell, NDAA Compliant, Embedded Network Video Recorders in 4 Channel, 8 Channel, 16 and 32 Channel varieties featuring storage ranging from 0 TB to 40 TB.  These NVRs feature secure, stream encryption via TLS 1.2, ONVIF S compliance, and H.265/H.264 Compression. Versions with the “C suffix” are MAXPRO Cloud Ready.

  - OPERATIONAL REQUIREMENTS

    - 35 Series NVR shall provide a user-friendly graphical user interface (GUI) to configure the cameras, create schedules for recording, perform video surveillance and recording operations, and view various reports.

      - 35 Series NVR shall be configured to store and view images captured by up to 16 cameras.

      - 35 Series NVR shall have the following major capabilities:

        - Record and monitor up to 16 IP channels with 1~30 fps per stream.

        - Network bandwidth/throughput supported per NVR:

          - HN350401xx/HN350802xx: 64 Mb

          - HN351602xx: 128 Mb

        - Support of up to 4 channels at 1080p H.265/H.264 decoding.

        - Live viewing of up to 16 channels simultaneously with synchronized real-time playback on your monitor.

        - Powerful investigation and video archive search tools from local or remote client.

        - Capable of managing motion detection-based recording, with pre-event and post-event recording based on IP camera-based motion detection events and “advanced” search on recordings from local or remote client.

        - Preview and Calendar Search permitting search for videos and events based on user-selected date and time from local or remote client.

        - Simultaneous use of multiple video compressions including H.265, H.264.

        - Internationalization – supports the following languages: English, Traditional Chinese, Japanese, German, Spanish, Italian, Polish, Portuguese, Russian, Slovakia, Arabic, Czech, Danish, Dutch, Finnish, French, Hebrew, Hungarian, Indonesian, Thai, Turkish, Vietnamese.

        - Email on alarm.

        - Dynamic IP Camera Discovery – Automatically discover all compatible cameras connected to the NVR.

        - Multi-level user access rights for viewing and manages access to the recorder functions.

        - Capable of managing continuous, scheduled, manual, event-based, and alarm-based recording features.

        - Support for web client and mobile apps.

      - Workstation (NVR Client) shall provide the following operator options:

        - Configuration: The operator (with Administrator privileges) shall have the option to configure the NVR. Live update of all configurations is supported. The following configurations shall be possible:

        - System Configuration: Provide options to configure the system level settings.

        - Camera Configuration: Provide options to add /delete IP cameras and modify the camera settings.

        - Schedules: Provide options to configure schedule-based recording for cameras connected to the NVR.

        - Sequences: Provide options to group a fixed number of cameras to view video.

        - User Management (Users, Groups and Roles): Provide option to add/edit/delete users and/or groups.

      - Configurations for cameras connected to the NVR:

        - Camera Configuration: The user shall be able to configure the following parameters for each camera connected to the NVR.

          - Camera Name

          - IP Address

          - Camera Type

          - Continuous Recording: All cameras added shall be defaulted to "24/7" recording with the option to select other recording modes.

          - Event Based Recording: Shall be “None” by default, with the option to select motion-based recording.

          - User name: Shall display and enable setting the user name for a camera.

          - Password: Shall enable setting the password for a camera.

          - Camera Advanced Settings: Shall enable configuration of Resolution, Video Frame Rate, and Video Bit Rate.

        - The following video recording options shall be supported:

          - Schedule-based recording: The system shall support the ability to schedule recordings for each individual camera for times in the future.

          - User-based recording: The user shall be able to configure user-activated settings for recording moments of interest while viewing live video from a camera. After configuring the user activated settings, the operator can start recording of video when needed. The video is recorded for the time period specified in the System settings for user activated recording.

          - Event-based recording: Event based recording shall be possible on Video Motion Detection and alarms triggered.

      - Viewer: The 35 Series NVR Viewer shall have the following minimum capabilities:

        - Main video viewing screen capable of showing 1-, 4-, 8-, 9-, 16- split salvos of live or recorded video. Standard presets shall be customizable to the user preferences.

        - Capable of configuring and running scan sequences.

        - Capable of setting the IP camera resolution and frame rate.

        - Capable of exporting user-selected image or video clips. A digital signature shall be attached to every exported clip.

        - Capability to play back the exported video clips. Each video channel that is being recorded by the recording system shall be overlaid with text and a time stamp that is customizable by the user.

        - Allow the user to initiate recording through the GUI or a controller.

        - Capability of complete alarm management for the alarms coming from the 35 Series NVR.

        - Playback control including play/pause, stop, rewind, fast play, slow play, frame-by-frame playback, full screen, and back up.

      - Search: The Search facility shall include search for recorded video and events based on date and time.

    - 35 Series PLUS NVR shall be configured to store and view images captured by up to 32 cameras.

      - 35 Series PLUS NVR shall have the following major capabilities:

        - Record and monitor up to 16 IP channels with 1~30 fps per stream.

        - Network bandwidth/throughput supported per NVR:

          - HN350802xxC: 80Mb

          - HN35160xxxC: 160Mb

          - HN353204xx/HN35320400N: 320Mb

          - HN350802xxC: Support of up to 8 channels at 1080p H.265/H.264 decoding

          - HN35160xxxC/HN353204xx/HN35320400N: Support of up to 9 channels at 1080p H.265/H.264 decoding

      - Live viewing of up to 32 channels or real-time playback of up to 16 channels

      - Powerful investigation and video archive search tools from local or remote client.

      - Capable of managing motion detection-based recording, with pre-event and post-event recording based on IP camera-based motion detection events and “advanced” search on recordings from local or remote client.

      - Preview and Calendar Search permitting search for videos and events based on user-selected date and time from local or remote client.

      - Simultaneous use of multiple video compressions including H.265, H.264.

      - Internationalization – supports the following languages: English, Traditional Chinese, Japanese, German, Spanish, Italian, Polish, Portuguese, Russian, Slovakia, Arabic, Czech, Danish, Dutch, Finnish, French, Hebrew, Hungarian, Indonesian, Thai, Turkish, Vietnamese.

      - Email on alarm.

      - Dynamic IP Camera Discovery – Automatically discover all compatible cameras connected to the NVR.

      - Multi-level user access rights for viewing and manages access to the recorder functions.

      - Capable of managing continuous, scheduled, manual, event-based, and alarm-based recording features.

      - Support for web client and mobile apps.

    - Workstation (NVR Client) shall provide the following operator options:

      - Configuration: The operator (with Administrator privileges) shall have the option to configure the NVR. Live update of all configurations is supported. The following configurations shall be possible:

        - System Configuration: Provide options to configure the system level settings.

        - Camera Configuration: Provide options to add /delete IP cameras and modify the camera settings.

        - Schedules: Provide options to configure schedule-based recording for cameras connected to the NVR.

        - Sequences: Provide options to group a fixed number of cameras to view video.

        - User Management (Users, Groups and Roles): Provide option to add/edit/delete users and/or groups.

    - Configurations for cameras connected to the NVR:

      - Camera Configuration: The user shall be able to configure the following parameters for each camera connected to the NVR.

        - Camera Name

        - IP Address

        - Camera Type

        - Continuous Recording: All cameras added shall be defaulted to "24/7" recording with the option to select other recording modes.

        - Event Based Recording: Shall be “None” by default, with the option to select motion-based recording.

        - User name: Shall display and enable setting the user name for a camera.

        - Password: Shall enable setting the password for a camera.

        - Camera Advanced Settings: Shall enable configuration of Resolution, Video Frame Rate, and Video Bit Rate.

      - The following video recording options shall be supported:

        - Schedule-based recording: The system shall support the ability to schedule recordings for each individual camera for times in the future.

        - User-based recording: The user shall be able to configure user-activated settings for recording moments of interest while viewing live video from a camera. After configuring the user activated settings, the operator can start recording of video when needed. The video is recorded for the time period specified in the System settings for user activated recording.

        - Event-based recording: Event based recording shall be possible on Video Motion Detection and alarms triggered.

    - Viewer: The 35 Series NVR Viewer shall have the following minimum capabilities:

      - Main video viewing screen capable of showing 1-, 4-, 8-, 9-, 16-, 32-, 64- split salvos of live or recorded video. Standard presets shall be customizable to the user preferences.

      - Capable of configuring and running scan sequences.

      - Capability to play back the exported video clips. Each video channel that is being recorded by the recording system shall be overlaid with text and a time stamp that is customizable by the user.

      - Allow the user to initiate recording through the GUI or a controller.

      - Capability of complete alarm management for the alarms coming from the 35 Series NVR.

      - Playback control including play/pause, stop, rewind, fast play, slow play, frame-by-frame playback, full screen, and back up.

    - Search: The Search facility shall include search for recorded video and events based on date and time.

  - SERIES INTEGRATIONS

    - The 35 Series NVR shall be compatible with the following interoperability standards:

      - Open Network Video Interface Forum (ONVIF)

      - Real Time Streaming Protocol (RTSP)

    - The 35 Series NVR shall be fully compatible with the 35 Series cameras.

    - NOTE TO SPECIFIER:  Some development may be required in specific user cases to support some of ONVIF protocols in the field as they mature over time.

  - SYSTEM HARDWARE

    - The 35 Series NVR shall have the following specifications:

      - Processor: ARM processor

      - Internal HDD:

        - HN350401xx/HN35040100N/HN35080100N: Internal x1 (3.5")

        - HN350802xx/HN351602xx/HN35160200N/HN35080200C/HN35080202C/

        - HN35080204C/HN35080208C/HN35080210C/HN35080216C/HN35160200C/HN35160204C/HN35160208C/HN35160210C/HN35160216C/HN35160220C: Internal x2 (3.5")

        - HN35160400C/HN35160404C/HN35160408C/HN35160410C/HN35160416C/HN35160420C/HN35320400/HN35320404/HN35320408/HN35320410/HN35320416/HN35320420/HN35320400N: Internal x4 (3.5")

      - Operating System: Embedded LINUX

      - Storage Capacities: 4 HDDs expandable up to 40 TB (10 TB per drive)

      - Video Storage Hard Disk Options: Internal fixed up to 10 TB SATA Hard Disk Drive options

      - Inputs and outputs:

        - Alarm Input:

          - HN350401xx/HN35040100N/HN35080100N: 4

          - HN350802xxC/HN35160xxxC/HN353204xx: 6

          - HN350802xx/HN351602xx/HN35160200N: 8

          - HN35320400N: 16

        - Alarm Out:

          - HN350401xx/HN350802xx/HN35040100N/HN35080100N/HN35160200N: 1

          - HN351602xx/ HN350802xxC/HN35160xxxC/HN353204xx: 2

          - HN35320400N: 4

      - Network Interface:

        - HN350401xx: 10/100Mbps Ethernet (RJ-45) x 1

        - HN35040100N/HN35080100N: 10/100Mbps Ethernet (RJ-45) x 2

        - HN350802xx/HN351602xx: 10/100/1000Mbps Ethernet (RJ-45) x 1

        - HN350802xxC/HN35160xxxC/HN353204xx/HN35160200N/HN35320400N: 10/100/1000Mbps Ethernet (RJ-45) x 2

      - Monitor Output:

        - HN350401xx/HN350802xx/HN351602xx/HN350802xxC/HN351602xxC /HN35040100N/HN35080100N/HN35160200N: HDMI x 1 (4K Max), VGA x1 (1080P)

        - HN351604xxC/HN353204xx: HDMI x 2 (only HDMI1 support 4k), VGA x1 (1080P)

      - Unit Dimensions:

        - HN350401xx/ HN35040100N/HN35080100N: 255.0 × 237.3 × 45.3 mm (10.04 × 9.34 × 1.78 inch)

        - HN350802xx/HN350802xxC/HN351602xx/HN351602xxC/HN35160200N: 372.0 × 313.3 × 46.5 mm (14.65 × 12.33 × 1.83 inch)

        - HN351604xxC/HN353204xx/HN35320400N: 440.0 × 376.2 × 70.0 mm (17.32 × 14.81 × 2.76 inch)

      - Unit Weight (Without HDD):

        - HN350401xx: 1 kg (2.20 lb) without HDD

        - HN350802xx/HN35160200N: 2.65 kg (5.84 lb) without HDD

        - HN35040100N/HN35080100N: 0.8 kg (1.76 lb) without HDD

        - HN35320400N: 4.5 kg (9.92 lb) without HDD

        - HN351602xx/HN351602xxC: 2.75 kg (6.05 lb) without HDD

        - HN350802xxC: 2.1 kg (4.63 lb) without HDD

        - HN351604xxC/HN353204xx: 4.65 kg (10.25 lb) without HDD

  - ELECTRICAL REQUIREMENTS

    - The 35 Series NVR shall have the following electrical specifications:

      - Power Supply: 100-240V AC, 50/60 Hz

      - Power Consumption:

        - HN350401xx:

          - Max. 65 W; 15W without HDD

          - Total PoE power consumption Max. 45W, 30 W for a single port

        - HN350802xx/HN351602xx//HN350802xxC/HN351602xxC:

          - Max. 180 W; 15W without HDD

          - Total PoE power consumption Max. 130 W, 30 W for a single port

        - HN351604xxC/HN353204xx:

          - Max. 300 W; 15W without HDD

          - Total PoE power consumption Max. 140 W, 30 W for a single port

        - HN35040100N/HN35080100N:

          - Max. 18 W;

          - 5W without HDD

        - HN35160200N:

          - Max. 24 W;

          - 5W without HDD

        - HN35320400N:

          - Max. 200 W;

          - 15W without HDD

  - ENVIRONMENTAL AND REGULATORY REQUIREMENTS

    - The 35 Series NVR shall be designed to meet the following environmental conditions:

      - Operating temperatures shall be between -10°C ~ 55°C (14°F ~ 131°F).

      - Storage temperatures shall be between –40°C ~ 60°C (-40°F ~ 140°F).

      - Relative Humidity: Less than 90% RH.

      - Emissions: FCC Part 15, CE (EN 55032, EN 61000-3-2, EN 61000-3-3, EN 61000-6-4), ICES-003, Comply with UKCA and RCM.

      - Immunity: CE(EN 50130-4, EN 55024, EN 55035) Comply with UKCA and RCM.

      - Safety: UL LISTED TO UL/CSA 62368-1, CE(EN 62368-1), Comply with UKCA and RCM.

      - RoHS: CE(EN 63000), UAE(Cabinet Decree No.10 of 2017).

  - WARRANTY

    - Manufacturer’s Guarantee: Five (5) years from the manufacture date code under normal use and service for the video surveillance system.

NOTE TO SPECIFIER: Delete if 70 Series cameras are not required

  - SYSTEMS DESCRIPTION

    - 70 AI Series cameras offer advanced artificial intelligence and smart video analytics capabilities enabling object categorization to improve situational awareness while reducing nuisance alarms. They deliver exceptional cybersecurity, license plate recognition capabilities, facial recognition (bullet & dome models), and excellent image quality even in low light conditions. Especially designed for Enterprise & Mission-Critical applications.

      - 8MP Outdoor Dome & Outdoor Bullet

      - 5MP In-Ceiling PTZ

  - OPERATIONAL REQUIREMENTS

    - 8MP Network TDN WDR IR Outdoor Dome Camera/Bullet Camera system shall meet or exceed the following camera specifications:

      - Image Sensor: 1/1.8”

      - Total Pixels: 3840 x 2160 (8 MP)

      - Minimum Illumination:

        - HC70W48R2: Color: 0.04 Lux @F1.5, B/W: 0Lux@F1.5 (IR on)

        - HC70WB8R2: Color: 0.04 Lux @F1.5, B/W: 0Lux @F1.5 (IR on)

      - WDR range: 120dB

      - Backlight Compensation: HLC/WDR

      - Day/Night: Auto/Day/Night/Synchronize with digital input/Schedule

      - Gain Control: 0-100%.

      - Noise Reduction: 3D DNR

      - Privacy Masking: Off / On (8 Areas)

      - Electronic Shutter Speed:

        - Manual: 1/2~1/ 10,000s

        - Shutter-Priority: 1/120~1 / 10,000s

      - Video Standard: NTSC/PAL

      - White Balance: Auto/Fixed Current/Manual

      - Signal-to-Noise Ratio: >50dB

      - Lens:

        - HC70W48R2: Remote Focus, 3.6 mm - 11 mm, MFZ, P-IRIS, F1.5 ~ F2.8

        - HC70WB8R2: Remote Focus, 3.6 mm - 11 mm, MFZ, P-IRIS, F1.5 ~ F2.8

      - Angle of View:

        - HC70W48R2: H: 105° ~ 49°, V: 58° ~ 28°

        - HC70WB8R2: H: 108° ~ 50°, V: 60° ~ 28°

      - Communication: ONVIF Profile S/G/T support.

    - 5MP Network TDN WDR Outdoor Speed Dome Camera system shall meet or exceed the following camera specifications:

      - Image Sensor: IMX335, 1/2.8” CMOS

      - Total Pixels: 2,592 × 1,944 (5 MP)

      - Minimum Illumination:

        - HC70WZ5I30: Color: 0.04 Lux @ F1.4; B/W: 0 Lux @ F1.4 (IR on)

        - HC70WZ5E30

          - Smoke Bubble:  Color: 0.5 Lux @ F1.4; B/W: 0.1 Lux @ F1.4

          - Clear Bubble:  Color:  Color: 0.5 Lux @ F1.4; B/W: 0 Lux @ F1.4

      - WDR range: 130dB

      - Backlight Compensation: WDR/BLC/HLC

      - Day/Night: Auto (ICR) / Color / BW

      - Noise Reduction: 3D DNR

      - Privacy Masking: Off / On (24 Areas)

      - Electronic Shutter Speed: 1/1 ~ 1/32000

      - Video Standard: NTSC/PAL

      - White Balance: Auto/Fixed Current/Manual

      - Signal-to-Noise Ratio: >50dB

      - Lens:

        - HC70WZ5I30: 30x Optical Zoom, Auto Focus, 5.2mm ~ 148.4mm, DC-IRIS, F1.3 ~ F4.8

      - Angle of View (H x V x D):

        - HC70WZ5I30: H: 55° ~ 2.64° V: 42° ~ 1.98° D: 65.4° ~2.5°

        - HC70WZ5E30:

      - 14 Communication: ONVIF Profile S/G/T support.

  - MECHANICAL REQUIREMENTS

    - 8MP Network TDN WDR IR Outdoor Camera system shall have the following mechanical specifications:

      - Unit Dimensions:

        - HC70WZ5I30:  222.0 mm x 267.5 mm x 124.07 mm (5.8” x 5.8” x 4.9”)

        - HC70WZ5E30:  147.89 mm x 147.89 mm x 124.07 mm (5.8” x 5.8” x 4.9”)

      - Dome Diameter: 147.89 mm (5.8”)

      - Product Weight: 1.08 kg (2.38 lb)

      - Body Material: Metal (die casting aluminum with power coating)

      - Bullet Camera:

      - Unit Dimensions: 104.9 mm x 104.9 mm x 267.4 mm (4.1” x 4.1” x 10.5”)

      - Product Weight: 1.75 kg (3.86 lb.)

      - Body Material: Metal (die casting aluminum with power coating)

    - 5MP Network TDN WDR Outdoor Speed Dome Camera system shall meet or exceed the following camera specifications:

      - Unit Dimensions:

        - HC70WZ5I30:  222 mm x 267.5 mm (8.74" x 10.53")

        - HC70WZ5E30: 217.8 mm x 266.3 mm (8.57" x 10.48")

      - Dome Diameter: 151.3 mm (6.0")

      - Product Weight:

        - HC70WZ5I30:  3.8 kg (8.38 lb.)

        - HC70WZ5E30:  4 kg (8.82 lb)

      - Body Material: Polycarbonate/Metal (die casting aluminum with powder coating)

  - ELECTRICAL REQUIREMENTS

    - 8MP Network TDN WDR IR Outdoor Camera system shall have the following electrical specifications:

      - Outdoor Dome Camera

        - Power Supply: 24VAC (50/60Hz), Heat On: PoE (IEEE 802.3af, Class 3)

        - Power Consumption: 13.5W

      - Bullet Camera

        - Power Supply: 24VAC (50/60Hz), Heat On: PoE (IEEE 802.3af, Class 4)

        - Power Consumption: 25 W

    - 5MP Network TDN WDR Outdoor Speed Dome Camera system shall have the following electrical specifications:

      - Power Supply:

        - HC70WZ5I30:  48VDC / 24VAC (50/60Hz), POE+

        - HC70WZ5E30:  48VDC / 24VAC (50/60Hz), POE++

      - Power Consumption:

        - HC70WZ5I30: 25 W

        - HC70WZ5E30: 30 W

  - ENVIRONMENTAL AND REGULATORY REQUIREMENTS

    - 8MP Network TDN WDR IR Outdoor Dome/Bullet Camera system shall be designed to meet the following environmental conditions and regulatory:

      - Operating temperature: Starting:

          - -40°C ~ 60°C (-40°F ~ 140°F) (802.3at PoE class4)

          - Working:

          - -40°C ~ 60°C (-40°F ~ 140°F) (802.3at PoE class4)

      - Relative Humidity: Less than 90%, non-condensing.

      - Emissions: FCC PART 15, CE (EN 55032)

      - Immunity: CE (EN 50130-4)

      - Safety: UL LISTED TO UL/CSA 62368-1, CE (EN 62368-1), UL/CSA 60950-22, CE (EN 60950-22)

      - RoHS: CE (EN 50581), EAC (TR EAEU 037/2016), UAE (Cabinet Decree No.10 of 2017)

      - Country or Region of Origin: Taiwan.

    - 5MP Network TDN WDR Outdoor Speed Dome Camera system shall be designed to meet the following environmental conditions and regulatory:

      - Operating temperature:

        - HC70WZ5I30:  -10°C ~ 50°C (14°F ~ 122°F)

        - HC70WZ5E30:  -40°C ~ 55°C (-40°F ~ 131°F)

      - Relative Humidity: 10% ~ 90%

      - Emissions: CE (EN 55032, EN 61000-3-2, EN 61000-3-3, EN 61000-6-4), FCC PART 15B, IECS-003, Comply with RCM and UKCA

      - Immunity: CE (EN 50130-4, EN 55035), Comply with RCM and UKCA

      - Safety: UL LISTED TO UL/CSA 62368-1, CE (EN 62368-1, EN 60950-22), Comply with RCM and UKCA

      - RoHS: CE (EN ICE 63000), UAE (Cabinet Decree No.10 of 2017)

      - Country or Region of Origin: Taiwan.

  - WARRANTY

    - Warranty: Five (5) years from the manufacture date code under normal use and service for the video surveillance system.

NOTE TO SPECIFIER: Delete if 60 Series cameras are not required

  - SYSTEM DESCRIPTION

    - 60 Series IP cameras suited for a wide range of indoor or outdoor applications. Choose from 4MP or 5MP dome or bullet cameras or 2MP or 5MP speed dome (PTZ) models. All models offer exceptional picture clarity, advanced video analytics built-in, secure data transmission and easy installation. Excellent fit for Enterprise & Critical Infrastructure applications.

  - OPERATIONAL REQUIREMENTS

    - 4MP Network TDN WDR IR Camera system shall meet or exceed the following camera specifications:

      - Image Sensor: 1/2.8” CMOS

      - Total Pixels: 2560 x 1440 (4 MP)

      - Minimum Illumination: 0.04 Lux @F1.4, B/W: 0Lux @F1.4(IR on)

      - WDR range: 120dB

      - Backlight Compensation: HLC/WDR

      - Day/Night: Auto/Day/Night/Synchronize with digital input/Schedule

      - Gain Control: 0-100%.

      - Noise Reduction: 3D DNR

      - Privacy Masking: Off / On (5 Areas)

      - Electronic Shutter Speed: 1/30 ~ 1/32000

      - Video Standard: NTSC/PAL

      - White Balance: Auto/Fixed Current/Manual

      - Signal-to-Noise Ratio: 60dB.

      - Lens: 2.7 mm ~ 13.5 mm, MFZ, P-IRIS, F1.4 ~ F2.8

      - Angle of View: H: 100° ~ 30°, V: 53° ~ 17°

      - Communication: ONVIF Profile S/G support.

    - 5MP Network TDN WDR IR Camera system shall meet or exceed the following camera specifications:

      - Image Sensor: 1/2.8” CMOS

      - Total Pixels: 2560 x 1920 (5 MP)

      - Minimum Illumination:

        - HC60Wx5R2: Color: 0.04 Lux @F1.4, B/W: 0Lux @F1.4(IR on)

        - HC60Wx5R4: Color: 0.04 Lux @F1.6, B/W: 0Lux @F1.6(IR on)

      - WDR range: 120dB

      - Backlight Compensation: HLC/WDR

      - Day/Night: Auto/Day/Night/Schedule

      - Gain Control: 0-100%.

      - Noise Reduction: 3D DNR

      - Privacy Masking: Off / On (5 Areas)

      - Electronic Shutter Speed: 1/32000 ~ 1/30

      - Video Standard: NTSC/PAL

      - White Balance: Auto/Fixed Current/Manual

      - Signal-to-Noise Ratio: 60dB.

      - Lens:

        - HC60Wx5R2: 2.7 mm ~ 13.5 mm, MFZ, P-IRIS, F1.4 ~ F2.8

        - HC60Wx5R4: 7 mm ~ 22 mm, MFZ, P-IRIS, F 1.6 ~ F2.9

        - HC60WB5R5: Remote Focus, 5 mm - 50 mm, MFZ, DC-IRIS, F1.9 ~ F2.1

      - Angle of View:

        - HC60Wx5R2: H: 100° ~ 30°, V: 72° ~ 23°

        - HC60Wx5R4: H: 39° ~ 16°, V: 29° ~ 12°

        - HC60WB5R5: H: 45° ~ 7°, V: 33° ~ 5°

      - Communication: ONVIF Profile S/G support.

    - 2MP Network TDN WDR Outdoor Speed Dome Camera system shall meet or exceed the following camera specifications:

      - Image Sensor: 1/2.8” CMOS

      - Total Pixels: 1920 x 1080

      - Minimum Illumination: Color: 0.1 Lux @F1.6, B/W: 0.005Lux @F1.6

      - WDR range: 120dB

      - Backlight Compensation: WDR, BLC, HLC

      - Day/Night: Auto/Day/Night/Synchronize with digital input/Schedule

      - Gain Control: Not support.

      - Noise Reduction: 3D DNR

      - Privacy Masking: Off / On (24 Areas)

      - Electronic Shutter Speed: 1/1 ~ 1/10000

      - Video Standard: NTSC/PAL

      - White Balance: Auto/Fixed Current/Manual

      - Signal-to-Noise Ratio: 55dB.

      - Lens: 30x Optical Zoom, Auto Focus, 4.3 mm ~ 129 mm, DC-IRIS, F1.6 ~ F4.7

      - Angle of View: H: 64°~2°, V: 36°~ 1°

      - Communication: ONVIF Profile S/G support.

      - RS485 interface: Pelco – D protocol.

    - 5MP/2MP Network TDN WDR Outdoor Speed Dome Camera system shall meet or exceed the following camera specifications:

        - Image Sensor: 1/2.8” CMOS

        - Total Pixels:

          - HC60WZ2R40: 1920 x 1080 px

          - HC60WZ5R30: 2560 x 1920 px

        - Minimum Illumination:

          - HC60WZ2R40: Color:  0.07 lux @F1.6 1/30sec BW: 0 lux @F1.6 (IR on)

          - HC60WZ5R30: Color:  0.04 lux @F1.4 1/30sec BW: 0 lux @F1.4 (IR on)

        - WDR range: 120dB

        - Backlight Compensation: WDR, BLC, HLC

        - Day/Night: Auto/Day/Night/Synchronize with digital input/Schedule

        - Gain Control: 0~100%.

        - Noise Reduction: 3D DNR

        - Privacy Masking: Off / On (24 Areas)

        - Electronic Shutter Speed: 1/1 ~ 1/100000

        - Video Standard: NTSC/PAL

        - White Balance: Auto/Fixed Current/Manual

        - Signal-to-Noise Ratio: >50dB.

        - Lens:

          - HC60WZ2R40: 40x Optical Zoom, Auto Focus, 4.25mm ~ 170mm, DC-IRIS, F1.6 ~ F4.95

          - HC60WZ5R30: 30x Optical Zoom, Auto Focus, 4.94mm ~ 148.24mm, DC-IRIS, F1.3 ~ F4.8

        - Angle of View:

          - HC60WZ2R40: H: 65.7° ~ 1.88°, V:39.4° ~ 1.09°

          - HC60WZ5R30: H: 54° ~ 2°, V:42° ~ 1.5°

        - Communication: ONVIF Profile S/G support.

        - RS485 interface: Pelco – D protocol.

  - MECHANICAL REQUIREMENTS

    - 4/5MP Network Indoor Dome Camera system shall have the following mechanical specifications:

      - Unit Dimensions: 126mm x 126mm x 122mm (4.96’’ x 4.96’’ x 4.8’’)

      - Dome diameter：91mm (3.58’’)

      - Product Weight: 1.75kg (3.86lb)

      - Material: Metal (die casting aluminum with liquid painting)

    - 4/5MP Network Outdoor Dome Camera system shall have the following mechanical specifications:

      - Unit Dimensions: 159mm x 159mm x 118.3mm (6.26’’ x 6.26’’ x 4.66’’)

      - Product Weight: 1.13kg (2.49lb)

      - Package Weight: 1.83kg (4.03lb)

      - Material: Metal (die casting aluminum with power coating)

      - Color: RAL 120-1 (Lyric White)

    - 4/5MP Network Outdoor Bullet Camera system shall have the following mechanical specifications:

      - Unit Dimensions: 104.6mm x 104.6mm x 277.5mm (4.12’’ x 4.12’’ x 10.93’’)

      - Product Weight: 1.75kg (3.86lb)

      - Package Weight: 1.78kg (3.92lb)

      - Body Material: Metal (die casting aluminum with power coating)

      - Color: RAL 120-1 (Lyric White)

    - 2MP Network TDN WDR Outdoor Speed Dome Camera system shall have the following mechanical specifications:

      - Unit Dimensions: 222.83mm x 222.83mm x 221.30mm (8.8’’ x 8.8’’ x 8.7’’)

      - Product Weight: 3.07kg (6.77lb)

      - Package Weight: 4.19kg (9.24lb)

      - Body Material: Metal (die casting aluminum with power coating)

    - 5MP/2MP Network TDN WDR Outdoor Speed Dome Camera system shall have the following mechanical specifications:

        - Unit Dimensions: Ø243.92 mm x 455.28 mm (Ø9.6”x17.9”)

        - Product Weight: 6.95kg (15.32lb)

        - Package Weight: 8.75kg (19.29lb)

        - Body Material: Aluminum and Plastic

  - ELECTRICAL REQUIREMENTS

    - 4MP Network Camera system shall have the following electrical specifications:

      - Input Voltage: 12VDC / 24VAC (50/60Hz), PoE (IEEE 802.3af, Class 0)

      - Power Consumption: 12.95W

    - 5MP Network TDN WDR IR Camera system shall have the following electrical specifications:

      - Power Supply: 12VDC / 24VAC (50/60Hz), Heat On: PoE (IEEE 802.3at, Class 4), Heat Off: PoE (IEEE 802.3at, Class 3)

      - Power Consumption: 25.5W

    - 2MP Network TDN WDR Outdoor Speed Dome Camera system shall have the following electrical specifications:

      - Input Voltage: 24VDC / 24VAC (50/60Hz), 60W UPOE

      - Power Consumption: 48 W/26 W (Heater on/off)

      - Voltage range of PTZ: AC/DC 22.8~25.2

    - 5MP/2MP Network TDN WDR Outdoor Speed Dome Camera system shall have the following electrical specifications:

        - Input Voltage: AC 24 V~, 3 A, 50-60 Hz ; or UPoE 42.5-57 V , MAX 51 W

        - Power Consumption: MAX 51 W

  - ENVIRONMENTAL AND REGULATORY REQUIREMENTS

    - 4/5MP Network WDR IR Indoor Dome Camera system shall be designed to meet the following environmental conditions and regulatory:

      - Operating temperature (IR OFF): Starting: 0°C ~ 60°C (32°F ~ 140°F), Working: -10°C ~ 60°C (14°F ~ 140°F)

      - Relative Humidity: Less than 90%, non-condensing.

      - Ingress Protection：IP52

      - Impact Resistance：IK10 (bubble only）

      - Emissions: FCC PART 15, CE (EN 55032)

      - Immunity: EN 50130-4

      - Safety: UL LISTED TO UL/CSA 62368-1, CE (EN 62368-1)

      - RoHS: CE (EN 50581), EAC (TR EAEU 037/2016), UAE (Cabinet Decree No.10 of 2017)

      - Country or Region of Origin: Taiwan.

    - 4MP Network WDR IR Outdoor Dome and Bullet Camera systems shall be designed to meet the following environmental conditions and regulatory:

      - Operating temperature (IR OFF): Starting: -10°C ~ 60°C (-40°F ~ 140°F), Working: -30°C ~ 60°C (-40°F ~ 140°F)

      - Relative Humidity: Less than 90%, non-condensing.

      - Ingress Protection：IP66/IP67

      - Impact Resistance：IK10

      - Emissions: FCC PART 15, CE (EN 55032)

      - Immunity: EN 50130-4

      - Safety: UL LISTED TO UL/CSA 62368-1, CE (EN 62368-1), UL/CSA 60950-22, CE (EN 60950-22)

      - RoHS: CE (EN 50581), EAC (TR EAEU 037/2016), UAE (Cabinet Decree No.10 of 2017)

      - Country or Region of Origin: Taiwan.

    - 5MP Network TDN WDR IR Outdoor Dome Camera system shall be designed to meet the following environmental conditions and regulatory:

      - Operating temperature: Starting: -40°C ~ 60°C (-40°F ~ 140°F), Working: -30°C ~ 60°C (-40°F ~ 140°F) (802.3 at PoE class4)

      - Relative Humidity: Less than 90%, non-condensing.

      - Ingress Protection：IP66/IP67

      - Impact Resistance：IK10

      - Emissions: FCC PART 15, CE (EN 55032)

      - Immunity: EN 50130-4

      - Safety: UL LISTED TO UL/CSA 62368-1, CE (EN 62368-1), UL/CSA 60950-22, CE (EN 60950-22)

      - RoHS: CE (EN 50581), EAC (TR EAEU 037/2016), UAE (Cabinet Decree No.10 of 2017)

      - Country or Region of Origin: Taiwan

    - 5MP Network TDN WDR IR Outdoor Bullet Camera system shall be designed to meet the following environmental conditions and regulatory:

      - Operating temperature: Starting: -40°C ~ 60°C (-40°F ~ 140°F) (802.3at PoE class4), Working: -40°C ~ 60°C (-40°F ~ 140°F) (802.3 at PoE class4)

      - Relative Humidity: Less than 90%, non-condensing.

      - Emissions: FCC PART 15, CE (EN 55032)

      - Immunity: CE (EN 50130-4)

      - Safety: UL LISTED TO UL/CSA 62368-1, CE (EN 62368-1), UL/CSA 60950-22, CE (EN 60950-22)

      - RoHS:  CE (EN 50581), EAC (TR EAEU 037/2016), UAE (Cabinet Decree No.10 of 2017)

      - Country or Region of Origin: Taiwan.

    - 2MP Network TDN WDR Outdoor Speed Dome Camera system shall be designed to meet the following environmental conditions and regulatory:

      - Operating temperature: Starting: -40°C ~ 60°C (-40°F ~ 140°F) (802.3at PoE class4), Working: -40°C ~ 60°C (-40°F ~ 140°F) (802.3 at PoE class4)

      - Relative Humidity: Less than 90%, non-condensing.

      - Emissions: FCC PART 15, CE (EN 55032)

      - Immunity: CE (EN 50130-4)

      - Safety: UL LISTED TO UL/CSA 62368-1, CE (EN 62368-1), UL/CSA 60950-22, CE (EN 60950-22)

      - RoHS:  CE (EN 50581), EAC (TR EAEU 037/2016), UAE (Cabinet Decree No.10 of 2017)

      - Country or Region of Origin: Taiwan.

    - 2MP/5MP Network TDN WDR Outdoor Speed Dome Camera system shall be designed to meet the following environmental conditions and regulatory:

      - Operating temperature: Starting: -40°C ~ 60°C (-40°F ~ 140°F) Working: -40°C ~ 60°C (-40°F ~ 140°F) (IR OFF)

      - Relative Humidity: Less than 90%, non-condensing.

      - Emissions: FCC PART 15, CE (EN 55032)

      - Immunity: CE (EN 50130-4)

      - Safety: UL LISTED TO UL/CSA 62368-1, CE (EN 62368-1), UL/CSA 60950-22, CE (EN 60950-22)

      - RoHS:  CE (EN 50581), UAE (Cabinet Decree No.10 of 2017)

      - Country or Region of Origin: Taiwan.

  - WARRANTY

    - Warranty: Five (5) years from the manufacture date code under normal use and service for the video surveillance system.

NOTE TO SPECIFIER: Delete if 35 Series cameras are not required

  - SYSTEM DESCRIPTION

    - Honeywell, NDAA Compliant, IP Cameras from 1080P up to 4K resolutions across 5 form factors including: PTZ, Micro Dome, Rugged Dome, Ball, and Bullet.  These cameras feature either a 2.8mm (Dome/Ball/Bullet) Fixed Lens, 2.8 – 12 mm MFZ Lens, 5-125 mm / 5-159 mm PTZ Lens with ONVIF S, G, T compliance, stream encryption, and built-in AI-based video analytics (PTZs, 5 & 8MP models).

  - OPERATIONAL REQUIREMENTS

    - 2MP/5MP TDN WDR IR PTZ Camera system shall meet or exceed the following camera specifications:

      - Image Sensor: 1/2.8” CMOS

      - Total Pixels:

        - HC35WZ2R25: 1920 x 1080

        - HC35WZ5R30: 2592 x 1944

      - Minimum Illumination: Color:  0.005 lux @F1.6 1/30sec BW: 0 lux @F1.6 (IR on)

      - WDR range: 120dB

      - IR Distance: up to 150 m

      - Backlight Compensation: WDR, BLC, HLC

      - Day/Night: Auto/Day/Night/Timing

      - Gain Control: 0~100%.

      - Noise Reduction: 2D/3D DNR

      - Privacy Masking: Off / On (5 Areas)

      - Electronic Shutter Speed: 1/1 ~ 1/30000

      - Video Standard: NTSC/PAL

      - White Balance: Auto/Tungsten/Daylight/Manual

      - Signal-to-Noise Ratio: >50 dB.

      - Lens:

        - HC35WZ2R25: 25x Optical Zoom, 16x Digital Zoom, Auto Focus, 5-125mm, P iris, F1.6-F3.67

        - HC35WZ5R30: 30x Optical Zoom, 16x Digital Zoom, Auto Focus, 5.3-159m, P iris, F1.6-F4.3

      - Angle of View:

        - HC35WZ2R25: H: 57.02° - 3.36°, V: 33.14° - 1.91°

        - HC35WZ5R30: H:56.62° - 2.48°, V:42.76° - 1.91°

      - Communication: ONVIF Profile S/G/T support

    - WDR 5 MP IR Micro Dome Camera system shall meet or exceed the following camera specifications:

      - Image Sensor: 1/2.8” 5 Megapixel progressive scan CMOS

      - Total Pixels: 2592x1944 (5 MP);

      - Minimum Illumination: 0.007 Lux/F2.0 (Color,30IRE), 0 Lux/F2.0 (IR ON)

      - WDR, ensuring glare-free images. WDR range: 120dB

      - IR Distance: up to 30 m

      - Backlight Compensation: WDR, BLC, HLC, Defog

      - Day/Night: Auto (ICR) / Color / BW.

      - Gain Control: 0-100%.

      - Noise Reduction: 2D/3D DNR.

      - Privacy Masking: Off / On (4 Areas).

      - Electronic Shutter Speed: 1/8 ~ 1/32,000.

      - Video Standard: NTSC/PAL.

      - Audio Interface:

        - HC35W25R3: 1 built-in microphone, 1 audio line in, 1 audio line out

      - Audio Compression: G711A/G711U

      - White Balance: Auto/Tungsten/ Fluorescent/ Daylight/Shadow/Manual.

      - Signal-to-Noise Ratio: More than 50dB.

      - Lens: 2.8mm, F2.0, fixed lens.

      - Angle of View:  H:88°, V:65°

      - Communication: ONVIF Profile S/G/T support.

    - WDR 3/5/8 MP IR MFZ Camera system shall meet or exceed the following camera specifications:

      - Image Sensor:

        - HC35Wx3R2: 1/2.7” 5 Megapixel progressive scan CMOS (Limited to 3M for use)

        - HC35Wx5R2: 1/2.8” 5 Megapixel progressive scan CMOS

        - HC35Wx8R2: 1/2.8” 8 Megapixel progressive scan CMOS

      - Total Pixels:

        - HC35Wx3R2: 2304x1296 (3 MP)

        - HC35Wx5R2: 2592x1944 (5 MP)

        - HC35Wx8R2: 3840x2160 (8 MP)

      - Minimum Illumination:

        - HC35Wx3R2/ HC35W45R2: 0.005 Lux/F1.6 (Color,30IRE), 0 Lux/F1.6 (IR ON)

        - HC35Wx8R2: 0.007 Lux/F1.6 (Color,30IRE), 0 Lux/F1.6 (IR ON)

      - WDR, ensuring glare-free images. WDR range: 120dB

      - IR Distance:

        - HC35W4xR2: up to 50 m

        - HC35WExR2: up to 50 m

        - HC35WBxR2: up to 60 m

      - Backlight Compensation: WDR, BLC, HLC, Defog

      - Note: HC35W43R2 doesn’t support defog.

      - Day/Night: Auto (ICR) / Color / BW.

      - Gain Control: 0-100%.

      - Noise Reduction: 2D/3D DNR.

      - Privacy Masking: Off / On (4 Areas).

      - Electronic Shutter Speed: 1/8 ~ 1/32,000.

      - Video Standard: NTSC/PAL.

      - Audio Interface:

        - HC35Wx3R2: not supported

        - HC35Wx5R2/ HC35Wx8R2: 1 audio line in, 1 audio line out

      - Audio Compression: G711A/G711U (HC35W43R2 not supported)

      - White Balance: Auto/Tungsten/ Fluorescent/ Daylight/Shadow/Manual.

      - Signal-to-Noise Ratio: More than 50dB.

      - Lens: 2.7-13.5mm, DC-Iris, F1.6-F3.3, MFZ Lens.

      - Angle of View:

        - HC35W43R2: H:88°-24° V:48°-14°

        - HC35W45R2: H:96°-26° V:69°-20°

        - HC35W48R2: H:105°-32° V:55°-18°

        - HC35WE3R2: H:81°-24° V:44°-14°

        - HC35WE5R2: H:87°-25° V:63°-19°

        - HC35WE8R2: H:98°-31° V:51°-17°

        - HC35WB3R2: H:81°-24° V:44°-14°

        - HC35WB5R2: H:88°-26° V:65°-20°

        - HC35WB8R2: H:98°-31° V:51°-17°

      - Communication: ONVIF Profile S/G/T support.

    - WDR 3/5/8 MP IR Fixed Camera system shall meet or exceed the following camera specifications:

      - Image Sensor:

        - HC35WB3R3: 1/2.7” 5 Megapixel progressive scan CMOS (Limited to 3M for use)

        - HC35WB5R3: 1/2.8” 5 Megapixel progressive scan CMOS

        - HC35WB8R3: 1/2.8” 8 Megapixel progressive scan CMOS

      - Total Pixels:

        - HC35WB3R3: 2304x1296 (3 MP)

        - HC35WB5R3: 2592x1944 (5 MP)

        - HC35WB8R3: 3840x2160 (8 MP)

      - Minimum Illumination:

        - HC35WB3R3: 0.005 Lux/F1.6 (Color,30IRE), 0 Lux/F1.6 (IR ON)

        - HC35WB5R3: 0.007 Lux/F2.0 (Color,30IRE), 0 Lux/F2.0 (IR ON)

        - HC35WB8R3: 0.009 Lux/F2.0 (Color,30IRE), 0 Lux/F2.0 (IR ON)

      - WDR, ensuring glare-free images. WDR range: 120dB

      - IR Distance:

        - HC35WExR3: up to 40 m

        - HC35WB3R3/HC35WB8R3: up to 40 m

        - HC35WB5R3: up to 50 m

      - Backlight Compensation: WDR, BLC, HLC, Defog

      - Note: HC35Wx3R3 doesn’t support defog.

      - Day/Night: Auto (ICR) / Color / BW.

      - Gain Control: 0-100%.

      - Noise Reduction: 2D/3D DNR.

      - Privacy Masking: Off / On (4 Areas).

      - Electronic Shutter Speed: 1/8 ~ 1/32,000.

      - Video Standard: NTSC/PAL.

      - Audio Interface:

        - HC35Wx3R3: not supported

        - HC35Wx5R3/ HC35Wx8R3: 1 audio line in, 1 audio line out

      - Audio Compression: G711A/G711U (HC35WB3R3 not supported)

      - White Balance: Auto/Tungsten/ Fluorescent/ Daylight/Shadow/Manual.

      - Signal-to-Noise Ratio: More than 50dB.

      - Lens: 2.8mm Fixed Iris F1.6, Fixed Lens.

      - Angle of View:

        - HC35WB3R3: H:88° V:47°

        - HC35WB5R3: H:88° V:65°

        - HC35WB8R3: H:97° V:52°

      - Communication: ONVIF Profile S/G/T support.

  - MECHANICAL REQUIREMENTS

    - 2MP/5MP TDN WDR IR PTZ Dome Camera system shall have the following mechanical specifications:

      - Unit Dimensions: Ø173.2 mm × 292.6 mm (Ø6.82” × 11.52”)

      - Product Weight: Approx. 3.5kg (7.71 lb.)

      - Material: Die-cast aluminum housing

    - WDR 5 MP IR Micro Dome Camera system shall have the following mechanical specifications:

      - Unit Dimensions: 104.9 mm x 104.9 mm x 63.3 mm (4.13”x 4.13” x 2.49”)

      - Dome diameter: Ø 56.4 mm (2.22”)

      - Product Weight: Approx. 0.55kg (1.21lb)

      - Material: Die-cast aluminum housing

    - WDR 3/5/8 MP IR MFZ Dome Camera system shall have the following mechanical specifications:

      - Unit Dimensions: Ø130.0 mm × 112.3 mm (Ø5.12” × 4.42”)

          - Dome diameter: Ø96.0 mm (3.78”)

      - Product Weight: Approx. 0.86 kg (1.90 lb.)

      - Material: Die-cast aluminum housing

    - WDR 3/5/8 MP IR Fixed Dome Camera system shall have the following mechanical specifications:

      - Unit Dimensions: Ø110.0 mm × 85.6 mm (Ø4.33” × 3.37”)

          - Dome Diameter: Ø78.2 mm (3.08”)

      - Product Weight: Approx. 0.56 kg (1.23 lb)

      - Material: Die-cast aluminum housing.

    - WDR 3/5/8 MP IR MFZ Bullet Camera system shall have the following mechanical specifications:

      - Unit Dimensions: Ø87.0 mm × 232.0 mm (Ø3.43” × 9.13”)

      - Product Weight: Approx. 0.92 kg (2.03 lb.)

      - Material: Die-cast aluminum housing

    - WDR 3/5/8 MP IR Fixed Bullet Camera system shall have the following mechanical specifications:

      - Unit Dimensions: Ø87.0 mm × 197.3 mm (Ø3.43” × 7.77”)

      - Product Weight: Approx. 0.7 kg (1.54 lb.)

      - Material: Die-cast aluminum housing

    - WDR 3/5/8 MP IR MFZ Ball Camera system shall have the following mechanical specifications:

      - Unit Dimensions: Ø126.1 x 114.0 mm (Ø4.96” × 4.49”)

      - Product Weight: Approx. 0.98 kg (2.16 lb.)

      - Material: Die-cast aluminum housing

    - WDR 3/5/8 MP IR Fixed Ball Camera system shall have the following mechanical specifications:

      - Unit Dimensions: Ø110.0 x 94.4 mm (Ø4.33” × 3.72”)

      - Product Weight: Approx. 0.6 kg (1.32 lb.)

      - Material: Die-cast aluminum housing

  - ELECTRICAL REQUIREMENTS

    - 2MP/5MP TDN WDR IR PTZ Dome Camera system shall have the following electrical specifications:

      - Input Voltage: AC 24 V~, 3 A, 50-60 Hz; or PoE+(IEEE 802.3at, Class4) 50-57 V, MAX 24 W

      - Power Consumption: MAX 24W

    - WDR 5 MP IR Micro Dome Camera system shall have the following electrical specifications:

      - Input Voltage:

      - HC35W25R3: DC12V 1A, PoE (IEEE 802.3af) (Class 0).

      - Power Consumption: MAX 4.2W

    - WDR 3/5/8 MP IR MFZ and Fixed Camera system shall have the following electrical specifications:

      - Input Voltage: DC12V 1A, PoE (IEEE 802.3af) (Class 0).

      - Power Consumption:

        - HC35WB3R2: MAX 5.5W

        - HC35WB5R2: MAX 6W

        - HC35WB8R2: MAX 7.3W

        - HC35W43R3: MAX 3.6W

        - HC35W45R3: MAX 4.08W

        - HC35W48R3: MAX 5.5W

        - HC35W43R2: MAX 5.5W

        - HC35W45R2: MAX 6W

        - HC35W48R2: MAX 6.7W

        - HC35WE3R2: MAX 5.5W

        - HC35WE5R2: MAX 6.11W

        - HC35WE8R2: MAX 6.7W

        - HC35WE3R3: MAX 5.5W

        - HC35WE5R3: MAX 5.13W

        - HC35WE8R3: MAX 6.4W

  - ENVIRONMENTAL AND REGULATORY REQUIREMENTS

    - 2MP/5MP TDN WDR IR PTZ Dome Camera system shall have the following environmental conditions and regulatory specifications:

      - Operating temperature:

      - Starting Temperature: -40°C ~ 60°C (-40°F ~ 140°F)

      - Working Temperature: -40°C ~ 70°C (-40°F ~ 158°F) (IR OFF)

      - Relative Humidity: Less than 90%, non-condensing.

      - Emissions: FCC PART 15, CE (EN 55032)

      - Immunity: CE (EN 50130-4), Complies with RCM and UKCA

      - Safety: UL LISTED TO UL/CSA 62368-1, CE (EN 62368-1), CE (EN 60950-22), Complies with RCM and UKCA

      - RoHS: CE (EN 63000), UAE (Cabinet Decree No.10 of 2017)

      - Country or Region of Origin: Vietnam.

    - WDR 5 MP IR Micro Dome Camera system shall have the following environmental conditions and regulatory specifications:

      - Operating temperature:

      - Starting Temperature: -40°C ~ 60°C (-40°F ~ 140°F)

      - Working Temperature: -40°C ~ 60°C (-40°F ~ 140°F) (IR OFF)

      - Relative Humidity: Less than 90%, non-condensing.

      - Emissions: FCC PART 15, CE (EN 55032)

      - Immunity: CE (EN 50130-4), Complies with RCM and UKCA

      - Safety: UL LISTED TO UL/CSA 62368-1, CE (EN 62368-1), CE (EN 60950-22), Complies with RCM and UKCA

      - RoHS: CE (EN 63000), UAE (Cabinet Decree No.10 of 2017).

      - Country or Region of Origin: Vietnam.

    - WDR 3/5/8 MP IR MFZ and Fixed Camera systems shall be designed to meet the following environmental conditions and regulatory specifications:

      - Operating temperature:

        - Starting Temperature: -40°C ~ 60°C (-40°F ~ 140°F)

        - Working Temperature: -40°C ~ 60°C (-40°F ~ 140°F) (IR OFF)

      - Relative Humidity: Less than 90%, non-condensing.

      - Emissions: FCC PART 15, CE (EN 55032)

      - Immunity: CE (EN 50130-4), Complies with RCM and UKCA

      - Safety: UL LISTED TO UL/CSA 62368-1, CE (EN 62368-1), CE (EN 60950-22), Complies with RCM and UKCA

      - RoHS: CE (EN 63000), UAE (Cabinet Decree No.10 of 2017).

      - Country or Region of Origin: Vietnam.

  - WARRANTY

    - Warranty: Warranty: Five (5) years from the manufacture date code under normal use and service for the video surveillance system.

NOTE TO SPECIFIER: Delete if 30 Series cameras are not required

  - SYSTEM DESCRIPTION

    - 5MP IP WDR IR Fisheye Camera, camera housing, cabling, and a web based GUI that provides complete control of camera settings and live video access.

  - OPERATIONAL REQUIREMENTS

    - 5MP IP WDR IR Fisheye Camera system shall meet or exceed the following camera specifications:

      - Image Sensor: 1/2.7” 5 Megapixel progressive scan CMOS

      - Total Pixels: 2560x1920

      - Minimum Illumination: 0.05lux color @ F2.25, 0 lux B/W with IRLEDs on @ F2.25

      - WDR, ensuring glare-free images. WDR range: 120dB

      - Backlight Compensation: HLC/WDR

      - Day/Night: Auto/Day/Night/Schedule.

      - Gain Control: 0-100%.

      - Noise Reduction: 3D DNR.

      - Privacy Masking: Off / On (5 Areas).

      - Electronic Shutter Speed: 1/5 ~ 1/32,000.

      - Video Standard: NTSC/PAL.

      - Dewarping mode:

        - Ceiling Mount: 1O/1P/1R/2P/1O3R/4R/4R PRO/1O8R;

        - Wall Mount:1O/1P/1R/1P2R/1O3R/1P3R/4R;

        - Floor Mount: 1O/1P/1R/2P/1O3R/4R/4R PRO/1O8R

      - Audio Interface: 1 built-in microphone

      - Audio Compression: G711/G726

      - White Balance: Auto/Fixed Current/Manual.

      - Signal-to-Noise Ratio: More than 55dB.

      - 1.16mm, Fixed, F2.25.

      - Angle of View: 180°

      - Communication: ONVIF Profile S/G support.

  - MECHANICAL REQUIREMENTS

    - 5MP IP WDR IR Fisheye Camera system shall have the following mechanical specifications:

      - Unit Dimensions: ø159.95mm x 59.7mm(ø6.3”x2.35”) (w/Mount plate)

        - ø159.95mm x 51.2mm(ø6.31”x 2.02”)

      - Product Weight: Approx. 0.82kg

      - Material: Die-casting aluminum housing with coating.

  - ELECTRICAL REQUIREMENTS

    - 5MP IP WDR IR Fisheye Camera system shall have the following electrical specifications:

      - Input Voltage: DC12V, PoE (IEEE 802.3af) (Class 0).

      - Power Consumption: MAX 10.8W

  - ENVIRONMENTAL AND REGULATORY REQUIREMENTS

    - 5MP IP WDR IR Fisheye Camera system shall be designed to meet the following environmental conditions and regulatory:

      - Operating temperature: –22°F (−30°C) to 140°F (60°C).

      - Relative Humidity: Less than 90%, non-condensing.

      - Emissions: FCC PART 15B, EN 55032, EN61000-6-3

      - Immunity: EN 50130-4

      - Safety: UL 62368-1, EN 62368-1

      - RoHS: EN 50581.

      - Country or Region of Origin: Taiwan.

  - WARRANTY

    - Warranty: Warranty: Five (5) years from the manufacture date code under normal use and service for the video surveillance system.

- EXECUTION

  - EXAMINATION

    - Examine site conditions to determine site conditions are acceptable without qualifications.  Notify Owner in writing if deficiencies are found.  Starting work is evidence that site conditions are acceptable.

  - PREPARATION

    - Clean surfaces thoroughly prior to installation.

    - Prepare surfaces using the methods recommended by the manufacturer for achieving the best result for the substrate under the project conditions.

  - INSTALLATION

    - System, including but not limited to access control, alarm monitoring and reporting, time management, and user identification cards shall be installed in accordance with the manufacturer's installation instructions.

    - Supervise installation to appraise ongoing progress of other trades and contracts, make allowances for all ongoing work, and coordinate the requirements of the installation of the System.

  - FIELD TESTING AND CERTIFICATION

    - Testing: The control, alarm monitoring and reporting, time management, and user identification cards shall be tested in accordance with the following:

    - Conduct a complete inspection and test of all installed access control and security monitoring equipment. This includes testing and verifying connection to equipment of other divisions such as life safety and elevators.

    - Provide staff to test all devices and all operational features of the System for witness by the Owner's representative and authorities having jurisdiction as applicable.

    - Correct deficiencies until satisfactory results are obtained.

    - Submit written copies of test results.

  - PROTECTION

    - Protect installed products until completion of project.

    - Touch-up, repair or replace damaged products before Substantial Completion.

END OF SECTION